## Method
10 Year Historic Data Method
Aoided Cost Definition | In the context of electricity planning, avoided T&D costs are the savings associated with the power system not having to deliver additional units of electricity, while still meeting the demand requirements of customers.
This method provides Avoided Costs based on peak demand of the T&D system and not with general energy sales reduction.
Measure | Carrying Charge for Average Annual Costs ($/yr) / Annual Coincident System Peak Load Growth (kW)
Data Source | T&D spreadsheet of last 10 Years of Capital Projects c/w Project to Date costing data
Methodology | For each year, identify: • Projects required due to load growth • Cost to Date of growth related transmission projects • Cost to Date of growth related distribution projects
Sum all transmission growth related costs after adjusting for inflation (2%/yr) Sum all distribution growth related costs after adjusting for inflation (2%/yr)
Divide both results by the number of years covered (10) to obtain Average Annual Cost in current year dollars
Determine Carrying Cost for Average Annual Costs ($/yr): = Average Annual Costs x Carrying Charge
Determine Historic Annual Growth Rate for the 10 year study period
Determine Constrained System Avoided T&D Costs ($/kw-yr): • Annual Constrained System growth (kW): = Sum of Constrained System Peak Load x Historic Annual Growth Rate • Avoided Transmission Costs: = Carrying Costs for Transmission Growth Projects ($/yr) / Annual Constrained System Growth (kW) • Avoided Distribution Costs: = Carrying Costs for Distribution Growth Projects ($/yr) /Annual Constrained System Growth (kW)
Determine System Wide Avoided T&D Costs ($/kw-yr): • Annual System Wide growth (kW): = 10 Year Linear Approximation of System Wide Peak Load Growth / 10 • Avoided Transmission Costs: = Carrying Costs for Transmission Growth Projects ($/yr) / Annual System Wide Growth (kW) • Avoided Distribution Costs: = Carrying Costs for Distribution Growth Projects ($/yr) / Annual System Wide Growth (kW)
Results | Results are developed on the 2010-2019 Projects tab and shown in the Results Summary

## Criteria
Assumptions for Identifying ACE Project Avoided T&D Cost Applicability
Assumption | T / D | Inclusions
1 | T | New Transmission Lines Required for Capacity
2 |  | Transmission Line Re-conductor / Re-tension Required for Capacity
3 |  | New EHV Transformer Required for Capacity
4 |  | New Substations (capacity / contingency capacity)
5 |  | Substation Capacity Upgrades (i.e. transformers)
6 | D | New distribution feeders
7 |  | Feeder re-conductoring
8 |  | Distribution Line Phase Conductor additions / extensions (load growth related)
9 |  | New voltage compensation / reactive devices (load growth related)
10 |  | Voltage conversions (load growth related)
Assumption | T / D | Exclusions
1 | T | Infrastructure replacements / upgrades required as a result of deteriorated plant or reliability upgrades
2 |  | Infrastructure upgrades associated with OATT Transmission Service Requests
3 |  | Infrastructure upgrades associated with Transmission Generator Interconnection Requests
4 |  | Infrastructure upgrades needed to meet new/updated NSPI/NPCC/NERC Standards
5 | D | Infrastructure replacements / upgrades required as a result of deteriorated plant or reliability upgrades
6 |  | Voltage conversions (reliability, updated standards, etc.)
7 |  | Upgrades/extensions/routines to connect new customers that are not avoidable costs
8 |  | Infrastructure upgrades associated with Distribution Generator Interconnection Requests

## Carrying Charge
Assumptions | Inputs
Total WACC - Interest / Carrying Cost | 6.616%
Estimated O&M Rate | 1%
Inflation Rate | 2%
Carrying Charge | 9.616%

## Interruptables
LARGE IND. INTERRUPTIBLE RIDER LOAD | 15-Minute | Supply
Contributor | Peak kW | Transmission | Distribution | T | D
1 | 1720.32 |  | 25kV |  | 1720.32
2 | 1439.52 |  | 12.5kV |  | 1439.52
3 | 1715.04 |  | 25kV |  | 1715.04
4 | 1794.72 |  | 25kV |  | 1794.72
5 | 1074.24 |  | 25kV |  | 1074.24
6 | 760.32 |  | 12.5kV |  | 760.32
7 | 43.2 |  | 12.5kV |  | 43.2
8 | 845.28 |  | 12.5kV |  | 845.28
9 | 12136.43 | 138kV |  | 12136.43
10 | 3800 | 69kV |  | 3800
11 | 3750.33 |  | 25kV |  | 3750.33
12 | 3223.92 | 69kV |  | 3223.92
13 | 3916.8 |  | 25kV |  | 3916.8
14 | 2567.04 |  | 25kV |  | 2567.04
15 | 16794.88 | 138kV |  | 16794.88
16 | 230.4 |  | 25kV |  | 230.4
17 | 1499 |  | 25kV |  | 1499
18 | 4684.8 | 69kV |  | 4684.8
19 | 10291.2 | 69kV |  | 10291.2
20 | 748.03 |  | 25kV |  | 748.03
21 | 213.12 |  | 25kV |  | 213.12
22 | 3039.67 | 69kV |  | 3039.67
23 | 2156.16 |  | 25kV |  | 2156.16
24 | 3186.4 | 69kV |  | 3186.4
25 | 6959.43 |  | 25kV |  | 6959.43
26 | 1849.44 |  | 25kV |  | 1849.44
27 | 4038.91 |  | 25kV |  | 4038.91
28 | 2552 |  | 25kV |  | 2552
29 | 4663 |  | 25kV |  | 4663
GR & L F LOAD | 15-Minute | Supply |  | 57157.3 | 44536.3
Contributor | Peak kW | Transmission | Distribution
1 | 0 | 138kV
2 | 1160.5 |  | 25kV
3 | 1304.96 |  | 25kV
4 |  | 69kV
5 |  | 69kV
Load Retention |  | Supply
Contributor | Peak kW | Transmission | Distribution
1 | 174858.44 | 138kV
Table values show Individual customer peak loads. Figure 2 of the 10 Year System Outlook Reports includes only the annual Interruptible Customer co-incident contribution to peak.
The data for this table was obtained from the Large Industrial & Commercial Customer Load Report (Jan/21)

## Results Summary
Avoided T&D Costs | Transmission $/kW-yr | Distribution $/kW-yr | Total $/kW-yr
Constrained System | 71.5797 | 62.321 | 133.9006
System Wide | 23.1983 | 20.1976 | 43.396
Note that a power Factor of 0.97 has been applied as a system average to convert Constrained System and System Wide growth in kVA to growth in kW.

## 2011-2020
Updated
Fp Number | CI | Matter | Funding Project Descr | Cc Cpc | Functional Class | Growth Related (y/n) | Notes | Routine Or Normal | Special Or Parent Routine | Work Order Status | In- Service Date | Complete Date | Proj To Date Actuals | Approval Type | FIN Date
39788-D312 | 39788 | #N/A | Highbury School Road - Part of D004 |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2011-01-20 | 2013-10-22 | 121737.49 | zINVALID FIN Approval - External | 2013-03-12 |  | 9 | 145487.5696
39929-D315 | 39929 | #N/A | East River Road Widening | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-01-31 | 2016-08-30 | 186861.82 | FIN Approval - Internal | 2016-09-12 |  | 9 | 223317.1724
39930-D316 | 39930 | #N/A | Middle Cape to Irishvale Upgrade |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-02-07 | 2013-08-12 | 670652.16 | zINVALID FIN Approval - Internal | 2013-08-12 |  | 9 | 801491.4125
38915-D294 | 38915 | #N/A | Martins Brook Regulation Additions | Dist - New | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-03-31 | 2014-07-23 | 116516.04 | FIN Approval - Internal | 2014-07-23 |  | 9 | 139247.4535
39644-D307 | 39644 | #N/A | Mill Village Teleglobe Line Removal |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-03-31 | 2014-08-08 | 44071.65 | FIN Approval - Internal | 2014-08-08 |  | 9 | 52669.7014
39664-D310 | 39664 | #N/A | 100H Bedford Substation Reliability |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-03-31 | 2013-10-22 | 239698.36 | zINVALID FIN Approval - External | 2013-04-16 |  | 9 | 286461.7287
40445-D327 | 40445 | #N/A | New Minas Traffic Circle |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-03-31 | 2012-11-15 | 176718.01 | zINVALID FIN Approval - External | 2012-10-30 |  | 9 | 211194.3805
40343-D335 | 40343 | #N/A | 73W-411 Mossman Lake Road |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-04-19 | 2013-10-22 | 20214.73 | zINVALID FIN Approval - External | 2013-03-13 |  | 9 | 24158.4736
38022-D360 | 38022 | #N/A | 2010 Recloser Additions |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-04-30 | 2013-10-22 | 1654443.36 | zINVALID FIN Approval - External | 2013-04-16 |  | 9 | 1977212.9647
38024-D361 | 38024 | #N/A | 2010 Dist. Cutout Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-04-30 | 2014-08-01 | 1962995.76 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 2345961.645
38062-D362 | 38062 | #N/A | 2010 Off Road to Roadside |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-04-30 | 2014-08-01 | 1120827.66 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 1339492.8072
38914-D305 | 38914 | #N/A | 2010 Guard Installations |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-05-20 | 2013-10-22 | 44895.15 | zINVALID FIN Approval - External | 2013-03-12 |  | 9 | 53653.8601
38867-D321 | 38867 | #N/A | Replacement of 3H and 6H Reclosers | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-06-30 | 2014-08-01 | 376975.08 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 450520.1167
40424-D325 | 40424 | #N/A | Highway Shift Pleasant St Yarmouth |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-06-30 | 2012-11-15 | 88793.96 | zINVALID FIN Approval - External | 2012-10-30 |  | 9 | 106117.0017
40263-D328 | 40263 | #N/A | 24C-442 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-07-19 | 2012-10-31 | 54206.13 | zINVALID FIN Approval - External | 2012-10-15 |  | 9 | 64781.3431
40264-D329 | 40264 | #N/A | 37N-411 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-07-19 | 2013-10-22 | 18134.33 | zINVALID FIN Approval - External | 2013-03-12 |  | 9 | 21672.203
40284-D332 | 40284 | #N/A | 82V-423 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-07-19 | 2016-03-31 | 48835.29 | zINVALID FIN Approval - External | 2013-04-16 |  | 9 | 58362.6922
40903-D354 | 40903 | #N/A | Campbell Hill Road Rebuild |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-07-19 | 2012-10-31 | 87390.27 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 104439.4622
39272-D370 | 39272 | #N/A | 2011 Distribution Feeder Ties | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-08-06 | 2016-04-30 | 614636.2 | FIN Approval - Internal | 2016-04-18 |  | 9 | 734547.155
38847-D367 | 38847 | #N/A | Distribution Feeder Ties |  | Distribution Plant - D | n |  | Normal |  | posted to CPR | 2011-08-08 | 2014-08-08 | 347465.23 | FIN Approval - Internal | 2014-08-08 |  | 9 | 415253.1142
40204-D342 | 40204 | #N/A | Starr Street Rebuild |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-08-24 | 2014-11-21 | 700082.5 | FIN Approval - Internal | 2014-11-21 |  | 9 | 836663.3932
40663-D346 | 40663 | #N/A | 1C-411 Port Hawkesbury Deter. Plant | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-08-24 | 2015-04-30 | 148484.46 | FIN Approval - Internal | 2016-02-18 |  | 9 | 177452.6747
40906-D364 | 40906 | #N/A | U&U Automatic Sleeve Replacement |  | Distribution Plant - D | n |  | Normal |  | posted to CPR | 2011-08-24 | 2014-11-21 | 287402.15 | FIN Approval - Internal | 2014-11-21 |  | 9 | 343472.1737
40248-D322 | 40248 | #N/A | Bell Museum |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-09-20 | 2012-10-30 | 99497.57 | zINVALID FIN Approval - External | 2012-09-27 |  | 9 | 118908.8065
40546-D336 | 40546 | #N/A | Cheticamp Deteriorated Insulators |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-09-20 | 2012-10-31 | 201332.68 | zINVALID FIN Approval - External | 2012-10-15 |  | 9 | 240611.1897
41357-D374 | 41357 | #N/A | Church St Line Relocation |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-09-29 | 2011-12-31 | 230861.19 |  |  |  | 9 | 275900.4926
40385-D368 | 40385 | #N/A | 88W-323G Pinkney's Point |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-09-30 | 2012-10-31 | 212259.95 | zINVALID FIN Approval - External | 2012-10-15 |  | 9 | 253670.2889
40762-D351 | 40762 | #N/A | Port Felix to Whitehead Part 2 | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-09-30 | 2016-01-31 | 433244.01 | FIN Approval - Internal | 2016-02-18 |  | 9 | 517766.6968
40904-D363 | 40904 | #N/A | 621V-Stepdown Conversion |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2011-09-30 | 2012-10-31 | 139198.39 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 166354.9615
40522-D326 | 40522 | #N/A | Dart Crossing Feeder Exit cables |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2011-10-03 | 2012-10-31 | 67301.14 | zINVALID FIN Approval - External | 2012-10-15 |  | 9 | 80431.0923
40943-D357 | 40943 | #N/A | Brunello Estates | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2011-10-03 | 2017-01-17 | 96988.28 | FIN Approval - Internal | 2017-01-17 |  | 9 | 115909.9727
40967-D358 | 40967 | #N/A | Brunello Estates Overhead | Dist - New | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2011-10-03 | 2016-01-31 | 68400.91 | zINVALID FIN Approval - Internal | 2016-02-18 |  | 9 | 81745.4192
40257-D323 | 40257 | #N/A | Spiddle Hill Wind Turbine |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-10-31 | 2015-04-30 | 7.79 | FIN Approval - Internal | 2015-04-17 |  | 9 | 9.3098
41668-D380 | 41668 | #N/A | Little River/Skir Dhu Hwy Shift |  | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2011-10-31 | 2012-10-31 | 111201.72 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 132896.3492
39270-D339 | 39270 | #N/A | 2011 Dist. Cutout Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2016-03-31 | 3217257.43 | zINVALID FIN Approval - External | 2013-04-16 |  | 9 | 3844920.4459
40265-D337 | 40265 | #N/A | 77V-401 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2013-10-22 | 207921.82 | zINVALID FIN Approval - External | 2013-03-12 |  | 9 | 248485.8219
40267-D330 | 40267 | #N/A | 37N-413 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2012-11-15 | 17747.45 | zINVALID FIN Approval - External | 2012-10-30 |  | 9 | 21209.8456
40268-D331 | 40268 | #N/A | 22N-401 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-11-21 | 86767.92 | FIN Approval - Internal | 2014-11-21 |  | 9 | 103695.6964
40273-D338 | 40273 | #N/A | 101H-411 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2016-03-31 | 54271.62 | zINVALID FIN Approval - External | 2012-10-30 |  | 9 | 64859.6097
40291-D333 | 40291 | #N/A | 2C-402 Targeted Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2013-10-22 | 47055.37 | zINVALID FIN Approval - External | 2013-03-12 |  | 9 | 56235.523
40300-D334 | 40300 | #N/A | 104H-432 Targeted Replacements | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2016-08-30 | 87209.15 | FIN Approval - External | 2016-09-12 |  | 9 | 104223.0071
40983-D365 | 40983 | #N/A | 70W-322 89W-301 Tie Line | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2011-12-20 | 2016-04-30 | 306130.9 | FIN Approval - Internal | 2016-04-18 |  | 9 | 365854.7636
41104-D369 | 41104 | #N/A | 1H-415 ICP Completion |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-12-20 | 2013-08-08 | 155509.23 | zINVALID FIN Approval - Internal | 2013-08-08 |  | 9 | 185847.9251
40227-D356 | 40227 | #N/A | 2011 Off Road to Roadside |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2014-11-25 | 2276117.63 | zINVALID FIN Approval - Internal | 2014-11-25 |  | 9 | 2720171.2649
40328-D353 | 40328 | #N/A | Feeder Exit Cable Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2014-08-01 | 485035.71 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 579662.5725
40662-D344 | 40662 | #N/A | 2011 Padmount Replacement Program | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-12-31 | 2016-08-30 | 648887.64 | FIN Approval - Internal | 2016-09-12 |  | 9 | 775480.7964
40712-D345 | 40712 | #N/A | Winslow Drive Makeready |  | Distribution Plant - D | n |  | Normal | D007 CONTRACTUAL REPLACEMENTS ROUTI | posted to CPR | 2011-12-31 | 2013-04-18 | -3512.66 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | -4197.9539
41364-D375 | 41364 | #N/A | 103W-311 Crandall Point Road |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-12-31 | 2012-10-31 | 98509.94 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 117728.4972
41803-D385 | 41803 | #N/A | 36V-302 Blomidon Deteriorated Poles | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-12-31 | 2016-01-31 | 54086.94 | FIN Approval - Internal | 2016-02-18 |  | 9 | 64638.9001
39269-D386 | 39269 | #N/A | 2011 Recloser Additions | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-01-31 | 2014-07-23 | 494632.78 | FIN Approval - Internal | 2014-07-23 |  | 8 | 579541.1368
40211-D348 | 40211 | #N/A | 2011 3H/6H Replacement Program |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-01-31 | 2014-07-11 | 339521.89 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 397804.0075
41326-D413 | 41326 | #N/A | 103C-311 Targeted Feeder Replacemen |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 129542.05 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 151779.1581
41332-D415 | 41332 | #N/A | 15S-302 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 137791.06 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 161444.1881
41342-D402 | 41342 | #N/A | 81S-301 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 102991.38 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 120670.8165
41343-D403 | 41343 | #N/A | 81S-302 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 231673.46 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 271442.3827
41344-D404 | 41344 | #N/A | 81S-305 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 163894.8 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 192028.8799
41345-D416 | 41345 | #N/A | 82S-303 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-27 | 2014-08-01 | 133749.95 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 156709.3836
40545-D349 | 40545 | #N/A | 2011 New Reliability Technologies |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-02-29 | 2014-07-23 | 78896.51 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 92439.8361
41033-D371 | 41033 | #N/A | Thistle Grove Subdivision Phase 1 | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2012-03-07 | 2016-04-30 | 24513.78 | FIN Approval - Internal | 2016-04-18 |  | 8 | 28721.8003
41204-D373 | 41204 | #N/A | 20H-305 Rebuild |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-03-12 | 2013-11-28 | 344057.16 | zINVALID FIN Approval - Internal | 2013-11-28 |  | 8 | 403117.7991
41328-D399 | 41328 | #N/A | 103W-312 Targeted Feeder Replacemen |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-03-12 | 2014-07-11 | 75136.12 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 88033.9399
41601-D376 | 41601 | #N/A | 686H - Lawerencetown Stepdown |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-03-12 | 2014-08-01 | 77021.14 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 90242.5412
41647-D379 | 41647 | #N/A | Grande Anse Voltage Reg Replacement |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-03-12 | 2014-07-23 | 43857.68 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 51386.2622
41398-D417 | 41398 | #N/A | 2012 Padmount Transformer Replaceme | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-03-31 | 2014-07-23 | 777646.34 | FIN Approval - Internal | 2014-07-23 |  | 8 | 911136.6294
41723-D387 | 41723 | #N/A | 85S-401 South Smokey Rebuild |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-04-25 | 2014-07-11 | 155526.77 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 182224.3991
41674-D384 | 41674 | #N/A | 15N -203 Truro Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-06-25 | 2016-01-31 | 81582.97 | FIN Approval - Internal | 2016-02-18 |  | 8 | 95587.4521
40320-D454 | 40320 | #N/A | LED Street Light Conversion | LED Streetlights | Distribution Plant - D | n |  | Normal | Special | in service | 2012-09-18 |  | 37754459.08 |  |  |  | 8 | 44235366.1557
41329-D400 | 41329 | #N/A | 11W-202 Voltage Conversion to 12 kV |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-08-01 | 120766.55 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 141497.2612
41334-D408 | 41334 | #N/A | 16N-301 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-11 | 178591.03 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 209247.8557
41337-D409 | 41337 | #N/A | 1N-405 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-11 | 184808 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 216532.0269
41338-D410 | 41338 | #N/A | 20H-301 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-11 | 610418.82 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 715202.9368
41340-D411 | 41340 | #N/A | 5N-301 Targeted Feeder Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-11 | 146834.33 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 172039.8202
41354-D441 | 41354 | #N/A | 519N-201 Partial Conversion 25KV |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-08-01 | 232933.62 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 272918.861
41646-D378 | 41646 | #N/A | 708H Columbus St Stepdown Conv |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-09-24 | 2013-11-28 | 65841.49 | zINVALID FIN Approval - Internal | 2013-11-28 |  | 8 | 77143.7994
42026-D396 | 42026 | #N/A | 70V-311 - Port Lorne Rebuild |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-09-24 | 2014-07-23 | 29665.08 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 34757.3693
42086-D406 | 42086 | #N/A | 509V-301 Central Grove Rebuild |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-09-24 | 2014-07-23 | 110082 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 128978.608
42088-D412 | 42088 | #N/A | 14C-211 Petit de Grat Re-Build |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-09-24 | 2014-08-01 | 291049.77 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 341011.1934
43367-D453 | 43367 | #N/A | Ridgewood Phase 2 |  | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2012-09-25 | 2013-11-28 | 64200.94 | zINVALID FIN Approval - Internal | 2013-11-28 |  | 8 | 75221.6336
41392-D395 | 41392 | #N/A | 2012 Distribution Cutout Replacemen | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2016-01-31 | 2528062.8 | FIN Approval - Internal | 2016-02-18 |  | 8 | 2962028.4954
41339-D440 | 41339 | #N/A | 2012 Distribution Feeder Ties | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-10-18 | 2017-07-21 | 736612 | FIN Approval - Internal | 2017-07-21 |  | 8 | 863058.36
41360-D428 | 41360 | #N/A | 82V-423 Hardwood Lands Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-10-18 | 2014-08-01 | 660248.68 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 773586.5597
39643-D309 | 39643 | #N/A | West River Station Reliability |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-10-22 | 2013-11-28 | 159445.37 | zINVALID FIN Approval - Internal | 2013-11-28 |  | 8 | 186815.6635
41926-D390 | 41926 | #N/A | Fairmount Interconnection | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2012-11-20 | 2019-09-30 | 0.03 | FIN Approval - Internal | 2019-07-31 |  | 8 | 0.03515
43098-D445 | 43098 | #N/A | 126H-421 Cobequid Rail Crossing |  | Distribution Plant - D | n |  | Normal | D007 CONTRACTUAL REPLACEMENTS ROUTI | posted to CPR | 2012-12-01 | 2014-08-01 | 115612.54 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 135458.5171
40224-D456 | 40224 | #N/A | 78W-301 Second Peninsula | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2016-04-30 | 623495.14 | FIN Approval - Internal | 2016-04-18 |  | 8 | 730523.9298
40329-D350 | 40329 | #N/A | Padmount Switchgear Replacement |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-23 | 70101.01 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 82134.506
41325-D434 | 41325 | #N/A | Replacmnt of 3H & 6H Reclosers 2012 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2017-06-23 | 346783.22 | FIN Approval - Internal | 2017-06-23 |  | 8 | 406311.8129
41351-D424 | 41351 | #N/A | 2012 Distribution Automation | Dist - New | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2016-12-14 | 270943.83 | FIN Approval - External | 2016-12-14 |  | 8 | 317453.8801
41353-D425 | 41353 | #N/A | 2012 Downline Recloser Additions |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-11 | 543663.85 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 636988.85
41356-D436 | 41356 | #N/A | 35V-312 Windsor Causeway |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-08-01 | 285010.01 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 333934.6519
41397-D420 | 41397 | #N/A | 2012 Padmount Switchgear Replacemen |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-08-01 | 128388.56 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 150427.6607
42592-D422 | 42592 | #N/A | 11S-303 Gang Switch & Circ Re-Conf |  | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2012-12-19 | 2014-08-01 | 139061.37 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 162932.5587
42830-D433 | 42830 | #N/A | 36V-302 Main St Canning Upgrade |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-12-19 | 2014-07-11 | 97990.28 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 114811.2308
42957-D443 | 42957 | #N/A | 70W-313 Lehave River Reconductor P1 |  | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-12-19 | 2014-07-11 | 464824.54 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 544616.0328
42958-D444 | 42958 | #N/A | CBRM Abandoned Pole Removal |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-12-19 | 2014-07-11 | 184821.85 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 216548.2544
43106-D466 | 43106 | #N/A | U&U 126H-311 Porter's Lake ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-23 | 214307.27 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 251095.1233
43161-D457 | 43161 | #N/A | U&U 18V-413 Upper Burlington ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-23 | 72048.71 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 84416.547
43178-D458 | 43178 | #N/A | 20H-302 - Sambro - Replacements U&U |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-08-01 | 68135.33 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 79831.3986
43185-D460 | 43185 | #N/A | U&U 22V-323G Prospect Rd ICP | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-23 | 32942.45 | FIN Approval - Internal | 2014-07-23 |  | 8 | 38597.3306
43196-D461 | 43196 | #N/A | U&U 4N-312 Tamagouche ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-11-21 | 62553.28 | zINVALID FIN Approval - Internal | 2014-11-21 |  | 8 | 73291.1373
43197-D462 | 43197 | #N/A | U&U 62N-413 Stellarton ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-11-21 | 123466.21 | zINVALID FIN Approval - Internal | 2014-11-21 |  | 8 | 144660.3432
43325-D451 | 43325 | #N/A | 62N-414 Spring Garden Road Re-Build |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-12-19 | 2014-07-11 | 70804.06 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 82958.2411
43352-D452 | 43352 | #N/A | 92H-333 Hiking Trail Pole Replace |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-12-19 | 2014-07-23 | 17720.35 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 20762.2143
43117-D446 | 43117 | #N/A | Prince Street Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-12-31 | 2017-01-17 | 162695.4 | FIN Approval - Internal | 2017-01-17 |  | 8 | 190623.5917
41388-D438 | 41388 | #N/A | 7H Beaufort Conversion |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-01-18 | 2014-08-01 | 347534.27 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 7 | 399207.635
41393-D405 | 41393 | #N/A | 2012 Automatic Sleeve Replacements |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-01-18 | 2014-08-01 | 283143.37 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 7 | 325242.731
43199-D463 | 43199 | #N/A | U&U 82V-402 Elmsdale ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-02-19 | 2014-07-11 | 9756.13 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 7 | 11206.7267
43546-D470 | 43546 | #N/A | 70W-313 Lehave River Reconductor | Dist - New | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-02-19 | 2016-01-31 | 257620.22 | FIN Approval - Internal | 2016-02-18 |  | 7 | 295924.6544
41349-D442 | 41349 | #N/A | 2012 Off Road To Roadside | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-03-27 | 2017-06-23 | 883413.71 | FIN Approval - Internal | 2017-06-23 |  | 7 | 1014764.6673
41797-D429 | 41797 | #N/A | Brier Island Crossing | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-03-27 | 2017-06-23 | 2579601.63 | FIN Approval - Internal | 2017-06-23 |  | 7 | 2963151.4206
42066-D397 | 42066 | #N/A | 85S-401 Insulator Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-03-27 | 2015-01-28 | 932305.9 | FIN Approval - Internal | 2015-01-28 |  | 7 | 1070926.4252
44127-D487 | 44127 | #N/A | 542W-311 East Berlin - Line Move |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-03-27 | 2014-07-23 | 23970.29 | FIN Approval - Internal | 2014-07-23 |  | 7 | 27534.3286
44052-D481 | 44052 | #N/A | 1N-404 Back Road Deteriorated Poles |  | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-05-22 | 2014-07-11 | 43745.11 | FIN Approval - Internal | 2014-07-10 |  | 7 | 50249.3809
44089-D485 | 44089 | #N/A | 57C-426H Sherbrooke Pole Replace | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-05-27 | 2014-08-01 | 46011.55 | FIN Approval - Internal | 2014-08-08 |  | 7 | 52852.808
41389-D465 | 41389 | #N/A | 8H Fairview Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-06-18 | 2016-12-22 | 1093420.49 | FIN Approval - Internal | 2016-12-22 |  | 7 | 1255996.4456
42829-D432 | 42829 | #N/A | Halifax Air Switch Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-06-18 | 2016-01-31 | 166745.44 | FIN Approval - Internal | 2016-02-18 |  | 7 | 191538.0971
43176-D467 | 43176 | #N/A | U&U 19W-312G Argyle Sound ICP | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-06-18 | 2016-12-14 | 329693 | FIN Approval - Internal | 2016-12-14 |  | 7 | 378713.6238
43198-D477 | 43198 | #N/A | 77V-302 - Conway - ICP | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-06-18 | 2014-07-23 | 124001.87 | FIN Approval - Internal | 2014-07-23 |  | 7 | 142439.1708
44088-D484 | 44088 | #N/A | 88W-312 BUNKER ISLAND LINE REMOVAL | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-06-18 | 2014-07-23 | 44612.99 | FIN Approval - Internal | 2014-07-23 |  | 7 | 51246.3022
44310-D492 | 44310 | #N/A | 14C-211 Petit de Grat Rebuild Pt 2 | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-06-18 | 2016-01-31 | 321120.97 | FIN Approval - Internal | 2016-02-18 |  | 7 | 368867.0558
43255-D475 | 43255 | #N/A | 2013 Distribution Cutout Replace | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-06-26 | 2016-09-12 | 398784.19 | FIN Approval - Internal | 2016-09-12 |  | 7 | 458077.6835
44771-D519 | 44771 | #N/A | Line Ext for Aerie Estates Ben Eion | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2013-07-17 | 2016-03-31 | -0.42 | FIN Approval - Internal | 2014-07-21 |  | 7 | -0.48245
41346-D464 | 41346 | #N/A | 82S-304 Whitney Pier Target Feeder | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2017-06-23 | 273918.46 | FIN Approval - Internal | 2017-06-23 |  | 7 | 314646.2091
43184-D459 | 43184 | #N/A | U&U 22C-404GAA ICP | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2016-12-14 | 193970.48 | FIN Approval - Internal | 2016-12-14 |  | 7 | 222811.1103
43194-D469 | 43194 | #N/A | 3S-303 North Sydney ICP | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2016-01-31 | 315864.32 | FIN Approval - Internal | 2016-02-18 |  | 7 | 362828.8173
44029-D478 | 44029 | #N/A | 62N-413 Fall Brook Road Re-build | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-08-31 | 2014-07-23 | 49293.02 | FIN Approval - Internal | 2014-07-23 |  | 7 | 56622.1856
44329-D500 | 44329 | #N/A | 11S-302/303 Keltic Drive Removals | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-08-31 | 2016-01-31 | 245712.12 | FIN Approval - Internal | 2016-02-18 |  | 7 | 282245.9906
44053-D482 | 44053 | #N/A | 79S Cape North Transformer Replace | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-09-25 | 2016-01-31 | 77914.18 | FIN Approval - Internal | 2016-02-18 |  | 7 | 89498.9019
44327-D499 | 44327 | #N/A | 77V-302 Beechwood Ln - Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-09-25 | 2014-07-23 | 43135.38 | FIN Approval - Internal | 2014-07-23 |  | 7 | 49548.9928
44346-D501 | 44346 | #N/A | 545W-311 Dagley Road - Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-09-25 | 2014-07-23 | 165629.47 | FIN Approval - Internal | 2014-07-23 |  | 7 | 190256.1983
43126-D474 | 43126 | #N/A | 13V-303 Bear River ICP | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-10-28 | 2016-12-14 | 418617.02 | FIN Approval - External | 2016-12-14 |  | 7 | 480859.3711
43192-D468 | 43192 | #N/A | U&U 25W-303 Shelburne ICP |  | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-10-28 | 2014-07-23 | 166638.04 | FIN Approval - External | 2014-07-23 |  | 7 | 191414.7282
44471-D514 | 44471 | #N/A | 36V-302 Main Street Canning | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-10-28 | 2016-01-31 | 218856.57 | FIN Approval - Internal | 2016-02-18 |  | 7 | 251397.4052
44630-D518 | 44630 | #N/A | 93V-313 Mardigrass Rd. Pole Replace | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-10-28 | 2016-08-30 | 29643.02 | FIN Approval - Internal | 2016-09-12 |  | 7 | 34050.5122
43286-D515 | 43286 | #N/A | 6S Terrace St Conversion Phase 1 | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-11-28 | 2016-01-31 | 1227430.88 | FIN Approval - Internal | 2016-02-18 |  | 7 | 1409932.2599
44227-D516 | 44227 | #N/A | 113H Dartmouth East Contingency U&U | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-11-28 | 2017-06-23 | 46231.76 | FIN Approval - Internal | 2017-06-23 |  | 7 | 53105.7601
43667-D473 | 43667 | #N/A | Kings Wharf Place | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2013-12-16 | 2017-01-17 | 155332.77 | FIN Approval - Internal | 2017-01-17 |  | 7 | 178428.5266
41672-D388 | 41672 | #N/A | Morris St/Water St Underground U&U | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-12-18 | 2016-02-28 | 948561.5 | FIN Approval - External | 2016-02-19 |  | 7 | 1089598.9999
43258-D495 | 43258 | #N/A | 2013 Offroad-to-Roadside | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-12-18 | 2017-07-21 | 1291498.17 | FIN Approval - Internal | 2017-07-21 |  | 7 | 1483525.4377
43276-D472 | 43276 | #N/A | 2013 Distribution Reliability Tech | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2013-12-18 | 2017-06-26 | 118887.52 | FIN Approval - Internal | 2017-06-26 |  | 7 | 136564.3903
43347-D455 | 43347 | #N/A | Eastern Voltage Regulator Replace | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-12-18 | 2014-07-23 | 52783.48 | FIN Approval - Internal | 2014-07-23 |  | 7 | 60631.627
44307-D511 | 44307 | #N/A | 16W-301 Port Maitland Rebuild | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-12-18 | 2016-01-31 | 120461.52 | FIN Approval - Internal | 2016-02-18 |  | 7 | 138372.4215
45739-D558 | 45739 | #N/A | 2014 Padmount Transformer Replace | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-01-08 | 2017-06-23 | 681996.1 | FIN Approval - Internal | 2017-06-23 |  | 6 | 768038.3779
41355-D435 | 41355 | #N/A | 2012 Remote Communication on Reclos | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-01-30 | 2017-06-27 | 232409.26 | FIN Approval - Internal | 2017-06-27 |  | 6 | 261730.5745
44529-D502 | 44529 | #N/A | IR 216 Granville Ferry | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2014-02-18 |  | 34403.06 |  |  |  | 6 | 38743.4333
41384-D421 | 41384 | #N/A | 2012 Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-02-28 | 2016-01-31 | 389950.17 | FIN Approval - Internal | 2016-02-18 |  | 6 | 439147.2268
41431-D431 | 41431 | #N/A | 1C-411/22C-404 Transfer Scheme | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-02-28 | 2017-06-23 | 204029.99 | FIN Approval - Internal | 2017-06-23 |  | 6 | 229770.9071
43189-D494 | 43189 | #N/A | 2013 Downline Recloser Additions | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-02-28 | 2016-09-12 | 248780.86 | FIN Approval - Internal | 2016-09-12 |  | 6 | 280167.6552
45046-D561 | 45046 | #N/A | 2014 PCB Phase-out for Pole Top | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-02-28 | 2017-07-21 | 644155.15 | FIN Approval - Internal | 2017-07-21 |  | 6 | 725423.3221
41358-D489 | 41358 | #N/A | 624V-311 Scotch Village Ph 3 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-03-21 | 2017-06-23 | 363013.89 | FIN Approval - Internal | 2017-06-23 |  | 6 | 408812.6006
44306-D491 | 44306 | #N/A | 16W-301 McCormack Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-03-26 | 2014-07-23 | 112836.57 | FIN Approval - Internal | 2014-07-23 |  | 6 | 127072.3047
44827-D537 | 44827 | #N/A | 2014 Distribution Cutout Replacemen | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-03-27 | 2016-01-31 | 106018.93 | FIN Approval - Internal | 2016-02-18 |  | 6 | 119394.5347
45514-D534 | 45514 | #N/A | Cabot Cliff Golf Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-03-28 | 2020-02-01 | 18276.45 | FIN Approval - Internal | 2019-07-31 |  | 6 | 20582.2511
41534-D389 | 41534 | #N/A | 2012 Reliability Technologies Dist. | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2014-04-22 | 2019-07-31 | 1258532.93 | FIN Approval - Internal | 2019-04-29 |  | 6 | 1417312.4892
45472-D538 | 45472 | #N/A | 12V-302 Allains Creek Crossing | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-05-15 | 2016-01-31 | 71928.23 | FIN Approval - Internal | 2016-02-18 |  | 6 | 81002.8695
45350-D531 | 45350 | #N/A | Evans Island | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2014-05-31 | 2020-05-01 | 45252.24 | FIN Approval - Internal | 2020-05-25 |  | 6 | 50961.3721
45412-D530 | 45412 | #N/A | Cabot Cliff Line Extension | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2014-06-30 | 2020-02-01 | -6917.56 | FIN Approval - Internal | 2019-07-31 |  | 6 | -7790.2961
45268-D536 | 45268 | #N/A | Queen Street Underground | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-08-31 | 2017-01-27 | 42074.56 | FIN Approval - Internal | 2017-01-27 |  | 6 | 47382.7883
45583-D553 | 45583 | #N/A | 682N -Greenfield Rd - Stepdown | Dist - New | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-08-31 | 2016-01-31 | 39647.71 | FIN Approval - Internal | 2016-02-18 |  | 6 | 44649.761
45880-D578 | 45880 | #N/A | Livingston Cove Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-10-09 | 2016-08-30 | 43748.49 | FIN Approval - Internal | 2016-09-12 |  | 6 | 49267.9053
45996-D588 | 45996 | #N/A | Shore Power Service Supply | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2014-10-28 | 2020-02-01 | 43644.42 | FIN Approval - Internal | 2020-02-28 |  | 6 | 49150.7056
43188-D493 | 43188 | #N/A | 2013 Distribution Automation | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2014-10-29 |  | 98927.9 |  |  |  | 6 | 111408.8832
45911-D575 | 45911 | #N/A | 698H Hunts Brook Rd Stepdown Upgrad | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-10-29 | 2016-01-31 | 29354.78 | FIN Approval - Internal | 2016-02-18 |  | 6 | 33058.2501
45652-D542 | 45652 | #N/A | 517W-311 - New Canada - Stepdown | Dist - New | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-11-24 | 2016-01-31 | 4222.58 | FIN Approval - Internal | 2016-02-18 |  | 6 | 4755.3109
46132-D585 | 46132 | #N/A | 81S-306 Hub Insulator Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-11-24 | 2016-01-31 | 34907.28 | FIN Approval - Internal | 2016-02-18 |  | 6 | 39311.2669
45877-D572 | 45877 | #N/A | 25N-201 Harrison Settlement Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-29 | 2017-06-23 | 155397.64 | FIN Approval - Internal | 2017-06-23 |  | 6 | 175002.9822
46459-D596 | 46459 | #N/A | 103W-312 Borgels Point Deter. Poles | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-29 | 2019-07-31 | 74691.45 | FIN Approval - Internal | 2019-04-29 |  | 6 | 84114.704
44388-D507 | 44388 | #N/A | 63V-313 Aylesford Reliability Ph 2 | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2017-01-17 | 513206.19 | FIN Approval - Internal | 2017-01-17 |  | 6 | 577953.5245
45870-D577 | 45870 | #N/A | 102W-311 - Chemin De L'Est | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2016-08-30 | 160324.81 | FIN Approval - Internal | 2016-09-12 |  | 6 | 180551.7759
45959-D582 | 45959 | #N/A | 629N-311 Hart Lake Pole Replacemen | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2016-01-31 | 164031.63 | FIN Approval - Internal | 2016-02-18 |  | 6 | 184726.2573
46010-D583 | 46010 | #N/A | 82V-402 637V Milford Stepdown | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-12-31 | 2016-01-31 | 20735.58 | FIN Approval - Internal | 2016-02-18 |  | 6 | 23351.6309
46030-D586 | 46030 | #N/A | 640V Mill Village Stepdown Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-12-31 | 2017-01-13 | 18705 | FIN Approval - Internal | 2017-01-16 |  | 6 | 21064.8681
46416-D598 | 46416 | #N/A | 16W-301 Ross Durkee Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2016-08-30 | 238976.72 | FIN Approval - Internal | 2016-09-12 |  | 6 | 269126.6011
46454-D599 | 46454 | #N/A | 519W Molega Lake Stepdown Replacmnt | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2019-12-31 | 61060.13 | FIN Approval - Internal | 2019-11-28 |  | 6 | 68763.6237
43273-D513 | 43273 | #N/A | 2013 Padmount Transformer Replace | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-01-08 | 2016-01-31 | 294092.44 | FIN Approval - Internal | 2016-02-18 |  | 5 | 324701.8174
45578-D554 | 45578 | #N/A | 55V-313J Waterville Recloser | Dist - New | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-01-08 | 2016-08-30 | 54321.92 | FIN Approval - Internal | 2016-09-12 |  | 5 | 59975.7891
46081-D589 | 46081 | #N/A | 70V-312H Thorne Rd Deteriorated Pol | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-01-08 | 2017-07-24 | 5315.18 | FIN Approval - Internal | 2017-07-24 |  | 5 | 5868.3882
46832-D616 | 46832 | #N/A | Katja Rose Dr 2014 | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2015-01-08 | 2020-02-01 | 16262.25 | FIN Approval - Internal | 2019-07-31 |  | 5 | 17954.838
43217-D573 | 43217 | #N/A | 24C-442G Hwy 16 Rebuild Ph 1 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-01-31 | 2019-04-01 | 830185.74 | FIN Approval - Internal | 2018-10-01 |  | 5 | 916592.1386
45820-D567 | 45820 | #N/A | Albany New Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-01-31 | 2017-07-21 | 151246.98 | FIN Approval - Internal | 2017-07-21 |  | 5 | 166988.8872
45730-D544 | 45730 | #N/A | Central Planned Deteriorated | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-02-28 |  | 2221779.64 |  |  |  | 5 | 2453024.2495
45734-D546 | 45734 | #N/A | West Planned Deteriorated Replace | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-02-28 |  | 2732582.52 |  |  |  | 5 | 3016991.9035
45735-D547 | 45735 | #N/A | Cent Unplanned Deteriorated Replace | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-02-28 |  | 1895120.62 |  |  |  | 5 | 2092366.2963
45736-D548 | 45736 | #N/A | East Unplanned Deteriorated Replace | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-02-28 |  | 518081.68 |  |  |  | 5 | 572004.0374
45737-D549 | 45737 | #N/A | West Unplanned Deteriorated Replace | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-02-28 |  | 1235223.19 |  |  |  | 5 | 1363786.2117
46620-D606 | 46620 | #N/A | 11S-411 Replace Hydraulic Reclosers | Dist - Replace / Refurb | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-02-28 | 2016-08-30 | 62679.3 | FIN Approval - Internal | 2016-09-12 |  | 5 | 69203.0119
45043-D581 | 45043 | #N/A | 57 Main Ave Primary Service Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-03-31 | 2020-01-01 | 10810.67 | FIN Approval - Internal | 2020-02-06 |  | 5 | 11935.8532
45799-D559 | 45799 | #N/A | Street Light & Service Removals | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-03-31 |  | 7831424.39 |  |  |  | 5 | 8646525.3307
46292-D625 | 46292 | #N/A | 2015 Padmount Replacement Program | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-03-31 | 2017-07-21 | 1461142.63 | FIN Approval - Internal | 2017-07-21 |  | 5 | 1613219.5285
46576-D627 | 46576 | #N/A | 2015 PCB Phase-out for Pole Top Tx | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-03-31 | 2017-07-21 | 756617.03 | FIN Approval - Internal | 2017-07-21 |  | 5 | 835366.3382
46738-D607 | 46738 | #N/A | Riverton COMFIT phases 1 & 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-05-30 | 2020-04-01 | 1039.24 | FIN Approval - Internal | 2020-03-25 |  | 5 | 1147.4049
46214-D595 | 46214 | #N/A | 16V-315 Windsor Deteriorated Poles | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-05-31 | 2017-01-20 | 248071.87 | FIN Approval - Internal | 2017-01-20 |  | 5 | 273891.3895
47216-D641 | 47216 | #N/A | 670N-Crowes Mills Overloaded Stepdo | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-05-31 | 2017-07-21 | 174897.64 | FIN Approval - Internal | 2017-07-21 |  | 5 | 193101.1268
47054-D632 | 47054 | #N/A | 22W-312 - Newellton Orion Wharf Rd | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-06-30 | 2017-07-21 | 33572.25 | FIN Approval - Internal | 2017-07-21 |  | 5 | 37066.4767
46737-D617 | 46737 | #N/A | 85S Gang Switch Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-08-31 | 2017-07-24 | 21133.23 | FIN Approval - Internal | 2017-07-24 |  | 5 | 23332.7936
47032-D629 | 47032 | #N/A | 65V-301 Mount Hanley Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-08-31 | 2017-07-21 | 52570.64 | FIN Approval - Internal | 2017-07-21 |  | 5 | 58042.2344
47122-D643 | 47122 | #N/A | 533N Pictou Landing Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-08-31 | 2017-06-23 | 108731.02 | FIN Approval - Internal | 2017-06-23 |  | 5 | 120047.8319
47159-D640 | 47159 | #N/A | 77V-302G North Range Cross Rd Rebld | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2015-08-31 |  | 42592.38 | FIN Approval - Internal | 2018-10-01 |  | 5 | 47025.4291
43234-D671 | 43234 | #N/A | 104S-313 Baddeck Re-build | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2015-09-30 |  | 957094.59 | FIN Approval - Internal | 2018-10-01 |  | 5 | 1056709.7637
43548-D525 | 43548 | #N/A | 533S Mason Street Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2015-09-30 |  | 790275.13 | FIN Approval - Internal | 2018-10-01 |  | 5 | 872527.6003
47223-D649 | 47223 | #N/A | 1N-403/405 Meeting House Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-06-23 | 96883.33 | FIN Approval - Internal | 2017-06-23 |  | 5 | 106967.0248
43203-D642 | 43203 | #N/A | 58C-405 Belle Cote Phase 1 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-10-31 | 2019-05-01 | 307312.64 | FIN Approval - Internal | 2019-02-11 |  | 5 | 339297.9864
47224-D677 | 47224 | #N/A | 1N-404 81N-411 Plains Rd Line Upgra | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-10-31 | 2017-07-21 | 240513.71 | FIN Approval - Internal | 2017-07-21 |  | 5 | 265546.5701
47494-D669 | 47494 | #N/A | 16W-302 Lake George Neutral Replace | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2015-10-31 | 2017-06-23 | 264236.1 | FIN Approval - Internal | 2017-06-23 |  | 5 | 291738.0055
46615-D611 | 46615 | #N/A | 613V-211 Bear River Voltage Convers | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-11-30 | 2017-07-21 | 163778.33 | FIN Approval - Internal | 2017-07-21 |  | 5 | 180824.5101
46619-D605 | 46619 | #N/A | 514C Lochaber Substation Impr. | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-11-30 | 2017-06-23 | 91649.16 | FIN Approval - Internal | 2017-06-23 |  | 5 | 101188.0782
47293-D656 | 47293 | #N/A | 22W-311 - Barrington Causeway to Ca | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-11-30 | 2017-06-23 | 61387.95 | FIN Approval - Internal | 2017-06-23 |  | 5 | 67777.2571
47294-D657 | 47294 | #N/A | 16V-315 New Edinburgh Rd | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-11-30 | 2017-07-21 | 100500.65 | FIN Approval - Internal | 2017-07-21 |  | 5 | 110960.8384
46971-D624 | 46971 | #N/A | 24C-443 Upgrade GUY Landfill | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-12-31 | 2020-02-01 | 1517.16 | FIN Approval - Internal | 2019-07-31 |  | 5 | 1675.0672
47840-D672 | 47840 | #N/A | Route 4 Highway Shift at Chapel Isl | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2015-12-31 | 2019-02-28 | 201738.72 | FIN Approval - Internal | 2018-06-29 |  | 5 | 222735.848
47292-D650 | 47292 | #N/A | 89W-302G - Rhodes Corner Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-01-31 | 2019-05-01 | 250596.63 | FIN Approval - Internal | 2019-02-11 |  | 4 | 271253.8515
47431-D662 | 47431 | #N/A | 666V-311-Castle Frederick Road - Re | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-01-31 | 2017-07-21 | 121358.21 | FIN Approval - Internal | 2017-07-21 |  | 4 | 131362.0294
43282-D497 | 43282 | #N/A | 2013 Distribution Feeder Ties | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-02-29 | 2019-07-31 | 510003.76 | FIN Approval - Internal | 2019-04-29 |  | 4 | 552044.4715
46456-D592 | 46456 | #N/A | 11W Yarmouth 4kV Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-02-29 | 2017-07-21 | 791983.17 | FIN Approval - Internal | 2017-07-21 |  | 4 | 857268.0534
47958-D681 | 47958 | #N/A | 538W-311 - Back Cornwall Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-02-29 | 2017-07-21 | 54084.52 | FIN Approval - Internal | 2017-07-21 |  | 4 | 58542.8238
43278-D517 | 43278 | #N/A | Halifax 4kV Conversion Part-1 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-07-31 | 388297.7 | FIN Approval - Internal | 2019-04-29 |  | 4 | 420305.9181
44826-D562 | 44826 | #N/A | 2014 Build-to-Roadside | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2016-03-31 |  | 806353.47 | FIN Approval - Internal | 2020-10-22 |  | 4 | 872822.9283
46736-D613 | 46736 | #N/A | Distribution Bulk Pole Purchase | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2021-01-01 | 241940.15 |  |  |  | 4 | 261883.7992
47773-D674 | 47773 | #N/A | 3N Oxford Conversion Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2016-03-31 |  | 720285.6 | FIN Approval - Internal | 2018-12-18 |  | 4 | 779660.2978
48711-D723 | 48711 | #N/A | 4C-441 Dagger Woods relocate | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2016-03-31 | 2020-02-01 | 239690.43 | FIN Approval - Internal | 2019-12-18 |  | 4 | 259448.6299
48731-D724 | 48731 | #N/A | 4C-441 Church St River Crossing | Distribution Line | Distribution Plant - D | n |  | Normal | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2016-03-31 | 2020-02-01 | 130433.68 | FIN Approval - Internal | 2019-07-31 |  | 4 | 141185.61
47778-D706 | 47778 | #N/A | 54H Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2016-04-30 |  | 116699.27 | FIN Approval - Internal | 2018-10-01 |  | 4 | 126319.0429
48416-D693 | 48416 | #N/A | Lower South River 515C | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-04-30 | 2018-08-31 | 16150.51 | FIN Approval - Internal | 2018-06-29 |  | 4 | 17481.8314
48575-D694 | 48575 | #N/A | 131H-421 Rossing Drive Feeder | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2016-04-30 | 2017-07-21 | 9920.72 | FIN Approval - Internal | 2017-07-21 |  | 4 | 10738.5064
48440-D713 | 48440 | #N/A | Upgrade R324-122 and R3A03781 | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2016-05-30 | 2017-07-21 | 24170.9 | FIN Approval - Internal | 2017-07-21 |  | 4 | 26163.3595
48752-D725 | 48752 | #N/A | 16N-302-Windham Hill-Deteriorated | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-05-30 | 2017-06-23 | 147328.94 | FIN Approval - Internal | 2017-06-23 |  | 4 | 159473.5828
48832-D726 | 48832 | #N/A | Voltage Regulator Replacement East | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2016-05-30 |  | 177543.11 | FIN Approval - Internal | 2018-10-01 |  | 4 | 192178.3721
48673-D721 | 48673 | #N/A | 3S-307 Epoxy Arm Changeout Sydney M | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-06-30 | 2017-06-23 | 102362.88 | FIN Approval - Internal | 2017-06-23 |  | 4 | 110800.8733
47721-D670 | 47721 | #N/A | 2016 PCB Phase-out for Pole Top Tx | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-07-31 | 2019-04-01 | 4199541.84 | FIN Approval - Internal | 2018-12-20 |  | 4 | 4545719.1449
47765-D704 | 47765 | #N/A | 58C-405 Belle Cote Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-07-31 | 2020-08-01 | 508943.46 | FIN Approval - Internal | 2020-01-27 |  | 4 | 550896.7687
47791-D708 | 47791 | #N/A | 103H Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-07-31 | 2017-07-21 | 121347.63 | FIN Approval - Internal | 2017-07-21 |  | 4 | 131350.5773
47811-D718 | 47811 | #N/A | Padmount Switch Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-07-31 | 2018-08-31 | 187678.95 | FIN Approval - Internal | 2018-06-29 |  | 4 | 203149.7312
47816-D678 | 47816 | #N/A | 660V-201 Duncan Ave Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-07-31 | 2017-06-23 | 142796.67 | FIN Approval - Internal | 2017-06-23 |  | 4 | 154567.7079
48069-D727 | 48069 | #N/A | Vault Upgrade Program | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2016-07-31 | 2019-02-28 | 65764.51 | FIN Approval - Internal | 2018-10-01 |  | 4 | 71185.6206
48093-D686 | 48093 | #N/A | 2016 Padmount Replacement Program | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-07-31 | 2020-08-01 | 1739040.03 | FIN Approval - Internal | 2020-03-25 |  | 4 | 1882392.856
48671-D716 | 48671 | #N/A | 19W-312 Dennis Point Wharf Reconduc | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-07-31 | 2017-07-21 | 210873.28 | FIN Approval - Internal | 2017-07-21 |  | 4 | 228256.02
41383-D418 | 41383 | #N/A | 2012 Halifax UG Feeder Cable Replmt | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-08-04 | 2020-05-01 | 533107.53 | FIN Approval - Internal | 2020-01-27 |  | 4 | 577052.7352
47766-D751 | 47766 | #N/A | 70V-312G Centerlea Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-08-04 | 2019-02-28 | 381586.91 | FIN Approval - Internal | 2018-11-28 |  | 4 | 413041.9432
48431-D709 | 48431 | #N/A | 36W-304G Enslow Point Road Line Rel | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2016-08-04 |  | 121781.11 | FIN Approval - Internal | 2018-10-01 |  | 4 | 131819.7899
49133-D742 | 49133 | #N/A | 4S-324 Hwy Relocation at Cow Bay Rd | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2016-08-25 | 2020-02-01 | 76270.42 | FIN Approval - Internal | 2019-07-31 |  | 4 | 82557.5555
49508-D750 | 49508 | #N/A | 67C-412 Seaside Comm Wireless Tower | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2016-08-29 | 2019-09-30 | 47759.52 | FIN Approval - Internal | 2019-07-31 |  | 4 | 51696.4404
49173-D743 | 49173 | #N/A | 11S-411 11S-302 Re-Build Coxheath | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2016-08-31 |  | 182268.97 | FIN Approval - Internal | 2018-10-01 |  | 4 | 197293.7949
49531-D759 | 49531 | #N/A | Jan 29, 2016 Level 3 Storm Response | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2016-08-31 | 2017-06-23 | 1512468.45 | FIN Approval - Internal | 2017-06-23 |  | 4 | 1637144.4913
48092-D685 | 48092 | #N/A | 2016 Subs Recloser Replacement | Substation Operations | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-09-30 | 2020-02-01 | 633511.76 | FIN Approval - Internal | 2019-08-23 |  | 4 | 685733.5028
48975-D731 | 48975 | #N/A | 59C-402G ICP-Device Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-09-30 | 2017-07-21 | 56631.98 | FIN Approval - Internal | 2017-07-21 |  | 4 | 61300.2764
49503-D755 | 49503 | #N/A | 57C-426 Amos Gillis Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-09-30 | 2017-07-21 | 18249.53 | FIN Approval - Internal | 2017-07-21 |  | 4 | 19753.8782
48652-D715 | 48652 | #N/A | 46V-303 Remove Abandoned Line | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-10-31 | 2017-07-21 | 19564.9 | FIN Approval - Internal | 2017-07-21 |  | 4 | 21177.677
49218-D767 | 49218 | #N/A | 49C Pomquet Forks Phase I | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2016-10-31 |  | 205561.39 | FIN Approval - Internal | 2018-10-01 |  | 4 | 222506.2594
49271-D752 | 49271 | #N/A | 505V-201 Weymouth Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-10-31 | 2019-05-01 | 127996.43 | FIN Approval - Internal | 2019-10-31 |  | 4 | 138547.4522
49498-D754 | 49498 | #N/A | 50N-410 / 50N-412 Reconfigure | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-10-31 | 2019-04-01 | 53587.5 | FIN Approval - Internal | 2018-10-01 |  | 4 | 58004.8334
45003-D652 | 45003 | #N/A | 2015 Hydraulic Recloser Repl. | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2016-11-30 | 2019-04-01 | 237079.49 | FIN Approval - Internal | 2019-01-03 |  | 4 | 256622.4645
46213-D591 | 46213 | #N/A | MicMac Mall Vault Upgrades | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-11-30 | 2017-07-21 | 141567.78 | FIN Approval - Internal | 2017-07-21 |  | 4 | 153237.5179
48432-D696 | 48432 | #N/A | 16W-301 Rodney Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2016-11-30 |  | 235281.26 | FIN Approval - Internal | 2018-10-01 |  | 4 | 254676.0025
48493-D690 | 48493 | #N/A | 581C Malignant Cove Voltage Reg | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-11-30 | 2019-04-01 | 115393.78 | FIN Approval - Internal | 2018-10-01 |  | 4 | 124905.9385
48974-D773 | 48974 | #N/A | McCabe Lake East Subdivision | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2016-12-20 | 2020-02-01 | 65481.2 | FIN Approval - Internal | 2019-07-31 |  | 4 | 70878.9568
44836-D684 | 44836 | #N/A | Halifax 4kV Conversion Part 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2016-12-31 |  | 768988.06 | FIN Approval - Internal | 2018-12-18 |  | 4 | 832377.4068
48976-D732 | 48976 | #N/A | 46W-301 Port Joli Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-12-31 | 2019-04-01 | 114626.83 | FIN Approval - Internal | 2018-12-20 |  | 4 | 124075.7672
49220-D768 | 49220 | #N/A | Antigonish Contingency Stepdowns | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2016-12-31 | 2017-07-21 | 123281.16 | FIN Approval - Internal | 2017-07-21 |  | 4 | 133443.4923
50031-D769 | 50031 | #N/A | 59C-402 Route 4 Reconductor | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-12-31 | 2018-08-31 | 473037.99 | FIN Approval - Internal | 2018-06-29 |  | 4 | 512031.5333
50032-D770 | 50032 | #N/A | Route 4 Highway Shift St. Peters | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2016-12-31 | 2019-05-01 | 208557.35 | FIN Approval - Internal | 2019-02-11 |  | 4 | 225749.1828
50341-D841 | 50341 | #N/A | 2017 Substn Recloser Replacements | Substation Operations | Distribution Plant - D | n |  | Normal | Special | in service | 2017-01-10 |  | 692360.97 |  |  |  | 3 | 734739.0003
50316-D776 | 50316 | #N/A | Oct 10, 2016 Level 3 Storm Response | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2017-01-25 | 2019-09-30 | 1712892.76 | FIN Approval - Internal | 2019-07-31 |  | 3 | 1817735.5001
50671-D798 | 50671 | #N/A | 627N-311-Spencer Point Rd-Pole Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-02-28 | 2019-05-01 | 31722.82 | FIN Approval - Internal | 2019-02-11 |  | 3 | 33664.5104
50711-D807 | 50711 | #N/A | 5N-301 Debert Beach Road Pole Replc | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-02-28 | 2019-04-01 | 12851.58 | FIN Approval - Internal | 2018-12-18 |  | 3 | 13638.1995
45031-D630 | 45031 | #N/A | 3N Oxford Conversion Phase 1 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-04-01 | 845160.57 | FIN Approval - Internal | 2018-12-18 |  | 3 | 896891.1582
47732-D699 | 47732 | #N/A | 131H-424/137H-412 Feeder Tie | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-05-01 | 302903.59 | FIN Approval - Internal | 2019-03-29 |  | 3 | 321443.7129
47760-D691 | 47760 | #N/A | 85S-402 Re-Insulate | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2020-11-01 | 1700924.43 | FIN Approval - Internal | 2020-06-17 |  | 3 | 1805034.6125
48195-D762 | 48195 | #N/A | Halifax 4kV Conversion Ph 3 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2020-11-01 | 520454.6 | FIN Approval - Internal | 2020-06-17 |  | 3 | 552310.5852
49791-D783 | 49791 | #N/A | 3N Oxford Conversion Phase 3 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2021-02-01 | 604785.22 | FIN Approval - Internal | 2020-10-01 |  | 3 | 641802.9137
49919-D778 | 49919 | #N/A | 2017 PCB Pole Top Trans. Replacemnt | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-03-31 |  | 1708846.23 |  |  |  | 3 | 1813441.29
50117-D772 | 50117 | #N/A | Moose River-Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2017-03-31 |  | -23888.35 |  |  |  | 3 | -25350.5081
50581-D795 | 50581 | #N/A | 585C-311 Jimtown Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-03-31 | 2020-02-01 | 136994.68 | FIN Approval - Internal | 2019-12-18 |  | 3 | 145379.8504
50653-D801 | 50653 | #N/A | 530N Thorburn Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-03-31 | 2019-05-01 | 20156.45 | FIN Approval - Internal | 2019-12-05 |  | 3 | 21390.186
50720-D809 | 50720 | #N/A | 641V-311G-Indian Rd-Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-03-31 | 2019-07-31 | 173521.68 | FIN Approval - Internal | 2019-04-29 |  | 3 | 184142.595
49806-D827 | 49806 | #N/A | 2017 Padmount Replacement Program | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-04-30 | 2020-11-01 | 1719177.15 | FIN Approval - Internal | 2020-06-17 |  | 3 | 1824404.545
50932-D837 | 50932 | #N/A | Feb 12, 2017 Level 3 Storm Response | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2017-04-30 | 2019-09-30 | 1081700.66 | FIN Approval - Internal | 2019-07-31 |  | 3 | 1147909.394
51211-D838 | 51211 | #N/A | Mar 14, 2017 Level 3 Storm Response | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2017-04-30 | 2020-03-01 | 228084.28 | FIN Approval - Internal | 2019-07-31 |  | 3 | 242044.8626
50575-D792 | 50575 | #N/A | 12V-302J-Milbury Lake Rd Repole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2017-05-30 |  | 101933.59 | FIN Approval - Internal | 2018-10-01 |  | 3 | 108172.7412
49191-D747 | 49191 | #N/A | 16V-314H St Bernard’s 3ph Extension | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-05-31 | 2019-04-01 | 101702.26 | FIN Approval - Internal | 2018-12-20 |  | 3 | 107927.2519
50611-D796 | 50611 | #N/A | 524C-201 Cape Jack Rd Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-05-31 | 2020-03-01 | 93146.56 | FIN Approval - Internal | 2019-02-11 |  | 3 | 98847.8746
50772-D845 | 50772 | #N/A | 37N-412 Glooscap Trail Rebuild Phas | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-05-31 | 2019-05-01 | 375232.25 | FIN Approval - Internal | 2019-02-11 |  | 3 | 398199.4656
11529-D002-611 | 11529 | #N/A | HALIFAX REGION - PRIMARY SERVICE RO |  | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-06-30 | 22391.69 |  |  |  | 3 | 23762.2406
14863-D002-735 | 14863 | #N/A | Customer Primary Services - Coldbro |  | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-07-24 | 603692.45 | FIN Approval - Internal | 2017-07-24 |  | 3 | 640643.2575
14874-D005-757 | 14874 | #N/A | SYDNEY REG. W. - REPLACE DETERIORAT |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 240.83 | FIN Approval - Internal | 2017-07-24 |  | 3 | 255.5707
14875-D005-758 | 14875 | #N/A | Sydney Reg. N. - Replace Deteriorat | Distribution Line | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | in service | 2017-06-30 |  | 6232.32 |  |  |  | 3 | 6613.7878
14911-D004-732 | 14911 | #N/A | NEW CUSTOMER REPLACEMENTS - BRIDGEW | Dist - New | Distribution Plant - D | n |  | Routine | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-06-30 | 2017-07-24 | 0.13 | FIN Approval - Internal | 2017-07-24 |  | 3 | 0.13796
14941-D005-734 | 14941 | #N/A | Replace Deteriorated Plant - Kentvi |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 3294.14 | FIN Approval - Internal | 2017-07-24 |  | 3 | 3495.7677
16113-D005-618 | 16113 | #N/A | Hfx Depot - Replace Det. Plant |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 5529.45 | FIN Approval - Internal | 2017-07-24 |  | 3 | 5867.8966
16119-D005-617 | 16119 | #N/A | DART. DEPOT - REPLACE DET. PLANT |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 635.09 | FIN Approval - Internal | 2017-07-24 |  | 3 | 673.9626
16125-D004-619 | 16125 | #N/A | ST. MARG. DEPOT- NEW CUST. REPLACEM |  | Distribution Plant - D | n |  | Routine | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-06-30 | 2017-06-30 | 40.46 |  |  |  | 3 | 42.9365
16814-D002-623 | 16814 | #N/A | Metro - Primary Services - Sackvill | Dist - Replace / Refurb | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-06-30 | 3001199.35 |  |  |  | 3 | 3184896.7598
17529-D002-752 | 17529 | #N/A | Sydney Region - Customer Primary Se |  | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-06-30 | 682728.18 |  |  |  | 3 | 724516.6064
18062-D003-752 | 18062 | #N/A | Sydney Region - New Customer Additi |  | Distribution Plant - D | n |  | Routine | D003 ADD.NEW CUST.ROUTINE | posted to CPR | 2017-06-30 | 2017-06-30 | -100.8 |  |  |  | 3 | -106.9698
26715-D002-800 | 26715 | #N/A | New Primary Services |  | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-06-30 | 2.62 |  |  |  | 3 | 2.7804
49604-D764 | 49604 | #N/A | 16V-314G Weymouth Falls Line Extens | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-06-30 | 2019-05-01 | 122457.29 | FIN Approval - Internal | 2019-02-11 |  | 3 | 129952.6558
50715-D808 | 50715 | #N/A | 108H-411 Simmonds Dr Pole Replc | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-06-30 | 2019-05-01 | 173274.17 | FIN Approval - Internal | 2019-02-11 |  | 3 | 183879.9354
50722-D811 | 50722 | #N/A | 88H-401-Higginsville Rd-Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-06-30 | 2019-04-01 | 81396.03 | FIN Approval - Internal | 2018-12-18 |  | 3 | 86378.1182
50796-D849 | 50796 | #N/A | New Distribution ROW Phase II | Vegetation Management | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-06-30 | 2019-02-28 | 3446611.94 | FIN Approval - Internal | 2018-10-01 |  | 3 | 3657572.1636
51493-D861 | 51493 | #N/A | 2018 PCB Pole Top Transformer Replc | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-06-30 |  | 1169635.83 |  |  |  | 3 | 1241226.8999
CONV-D002-811 | D002-811 | #N/A | D002-Cust.primary Service |  | Distribution Plant - D | n |  | Routine | D002-CUST.PRIMARY SERVICE | posted to CPR | 2017-06-30 | 2017-06-30 | 26098.87 |  |  |  | 3 | 27696.3296
CONV-D003-623 | D003-623 | #N/A | D003 Add.new Cust.routine | Distribution Line | Distribution Plant - D | n |  | Routine | D003 ADD.NEW CUST.ROUTINE | posted to CPR | 2017-06-30 | 2017-06-30 | -232.42 |  |  |  | 3 | -246.646
CONV-D004-629 | D004-629 | #N/A | D004 NEW CUSTOMER REPLACEMENTS.ROUT |  | Distribution Plant - D | n |  | Routine | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-06-30 | 2017-06-30 | 816.93 |  |  |  | 3 | 866.9327
CONV-D004-743 | D004-743 | #N/A | D004 NEW CUSTOMER REPLACEMENTS.ROUT |  | Distribution Plant - D | n |  | Routine | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-06-30 | 2017-07-24 | 450.88 | FIN Approval - Internal | 2017-07-24 |  | 3 | 478.4775
CONV-D004-811 | D004-811 | #N/A | D004 NEW CUST REPLACE DoNotUse | Distribution Line | Distribution Plant - D | n |  | Routine | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2017-06-30 |  | 12552.47 |  |  |  | 3 | 13320.7816
CONV-D005-628 | D005-628 | #N/A | D005 Replace Deteriorated Plant Rou |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 10.41 | FIN Approval - Internal | 2017-07-24 |  | 3 | 11.0472
CONV-D005-629 | D005-629 | #N/A | D005 REPLACE DETERIORATED PLANT ROU |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 112.05 | FIN Approval - Internal | 2017-07-24 |  | 3 | 118.9084
CONV-D005-713 | D005-713 | #N/A | D005 REPLACE DETERIORATED PLANT ROU |  | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | posted to CPR | 2017-06-30 | 2017-07-24 | 466.18 | FIN Approval - Internal | 2017-07-24 |  | 3 | 494.7139
14878-D006-756 | 14878 | #N/A | Sydney Reg. E. - Regulatory Replace |  | Distribution Plant - D | n |  | Routine | D006 REGULATORY REPLACEMENTS | completed | 2017-07-24 | 2017-07-24 | 262.62 | FIN Approval - Internal | 2017-07-24 |  | 3 | 278.6944
14985-D006-611 | 14985 | #N/A | REGULATORY REPLACEMENTS - HALIFAX |  | Distribution Plant - D | n |  | Routine | D006 REGULATORY REPLACEMENTS | completed | 2017-07-24 | 2017-07-24 | 356.2 | FIN Approval - Internal | 2017-07-24 |  | 3 | 378.0023
16831-D016-623 | 16831 | #N/A | New Customers - Services Unmetered |  | Distribution Plant - D | n |  | Routine | D016-SERVICES UNMETERED-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 999874.74 | FIN Approval - Internal | 2017-07-24 |  | 3 | 1061075.0731
16832-D017-623 | 16832 | #N/A | New Customers - Metered Service Dro |  | Distribution Plant - D | n |  | Routine | D017-METERED SERVICE DROPS-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 12211005.11 | FIN Approval - Internal | 2017-07-24 |  | 3 | 12958416.3108
16835-D021-623 | 16835 | #N/A | New Customers -Primary Line Ext CEN |  | Distribution Plant - D | n |  | Routine | D021-PRIMARY LINE EXTENSIONS-ROUTIN | completed | 2017-07-24 | 2017-07-24 | 3877205.28 | FIN Approval - Internal | 2017-07-24 |  | 3 | 4114521.2608
25077-D016-735 | 25077 | #N/A | New Cust Unmetered Serv WST |  | Distribution Plant - D | n |  | Routine | D016-SERVICES UNMETERED-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 306690.56 | FIN Approval - Internal | 2017-07-24 |  | 3 | 325462.4758
25078-D016-752 | 25078 | #N/A | New Customers- Unmetered Services S |  | Distribution Plant - D | n |  | Routine | D016-SERVICES UNMETERED-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 635133.71 | FIN Approval - Internal | 2017-07-24 |  | 3 | 674008.9741
25080-D017-735 | 25080 | #N/A | New Customers - Metered Services We |  | Distribution Plant - D | n |  | Routine | D017-METERED SERVICE DROPS-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 5097221.45 | FIN Approval - Internal | 2017-07-24 |  | 3 | 5409212.1805
25081-D017-752 | 25081 | #N/A | New Customers - Metered Services Fo |  | Distribution Plant - D | n |  | Routine | D017-METERED SERVICE DROPS-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 5342649.51 | FIN Approval - Internal | 2017-07-24 |  | 3 | 5669662.4012
26717-D016-800 | 26717 | #N/A | New Cust Unmetered Serv PROV | Distribution Line | Distribution Plant - D | n |  | Routine | D016-SERVICES UNMETERED-ROUTINE | completed | 2017-07-24 | 2017-07-24 | -1824.75 | FIN Approval - Internal | 2017-07-24 |  | 3 | -1936.4393
26718-D017-800 | 26718 | #N/A | New Customers - Metered Services | Distribution Line | Distribution Plant - D | n |  | Routine | D017-METERED SERVICE DROPS-ROUTINE | completed | 2017-07-24 | 2017-07-24 | 251904.82 | FIN Approval - Internal | 2017-07-24 |  | 3 | 267323.4102
26719-D021-800 | 26719 | #N/A | New Customers -Line Extensions PROV | Distribution Line | Distribution Plant - D | n |  | Routine | D021-PRIMARY LINE EXTENSIONS-ROUTIN | completed | 2017-07-24 | 2017-07-24 | 947592.74 | FIN Approval - Internal | 2017-07-24 |  | 3 | 1005592.9964
CONV-D008-628 | D008-628 | #N/A | D008-Storm Costs Routine |  | Distribution Plant - D | n |  | Routine | D008-STORM COSTS ROUTINE | completed | 2017-07-24 | 2017-07-24 | 10.41 | FIN Approval - Internal | 2017-07-24 |  | 3 | 11.0472
46623-D666 | 46623 | #N/A | Rights for Facility on Railway Land | AMO - Customer Operations | Distribution Plant - D | n |  | Normal | Special | in service | 2017-07-31 |  | 29834.4 |  |  |  | 3 | 31660.504
48071-D736 | 48071 | #N/A | 2016 Manhole Cover Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-07-31 | 2018-08-31 | 53588.96 | FIN Approval - Internal | 2018-06-29 |  | 3 | 56869.0331
49113-D741 | 49113 | #N/A | 12V-303G - Clementsport Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-07-31 | 2019-04-01 | 129382.28 | FIN Approval - Internal | 2018-12-20 |  | 3 | 137301.5106
49611-D780 | 49611 | #N/A | New Distribution ROW Phase 1 | Vegetation Management | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2020-08-01 | 2055132.49 | FIN Approval - Internal | 2020-06-17 |  | 3 | 2180923.0394
49862-D846 | 49862 | #N/A | 50N-410 Rebuild Trenton | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2019-07-31 | 486542.03 | FIN Approval - Internal | 2019-04-29 |  | 3 | 516322.2946
49918-D779 | 49918 | #N/A | 54H-303 Underground Device Replacem | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2019-05-01 | 521501.35 | FIN Approval - Internal | 2019-02-11 |  | 3 | 553421.4046
50576-D793 | 50576 | #N/A | 73W-411GCA-Chesley Rd Repole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2017-07-31 |  | 52284.23 | FIN Approval - Internal | 2018-10-01 |  | 3 | 55484.4431
50655-D802 | 50655 | #N/A | 664N-211 Claremont Avenue Conversio | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-07-31 | 2019-09-30 | 148636.76 | FIN Approval - Internal | 2019-07-31 |  | 3 | 157734.5188
50673-D800 | 50673 | #N/A | 49C Pomquet Forks Conversion Ph 2 | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-07-31 | 2019-05-01 | 92508.02 | FIN Approval - Internal | 2019-02-11 |  | 3 | 98170.2509
51071-D835 | 51071 | #N/A | 4C-430G Old Maryvale Road Pole Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-07-31 | 2019-12-31 | 36050.2 | FIN Approval - Internal | 2019-11-28 |  | 3 | 38256.7606
51412-D848 | 51412 | #N/A | 87H-313G Harbourview Dr Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2017-07-31 | 2019-05-01 | 97950.92 | FIN Approval - Internal | 2019-03-29 |  | 3 | 103946.2999
C0002898 | C0002898 | #N/A | Little Narrow Underwater Cable Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D005 REPLACE DETERIORATED PLANT ROU | in service | 2017-07-31 |  | 449550.31 | FIN Approval - Internal | 2020-06-11 |  | 3 | 477066.3854
49863-D818 | 49863 | #N/A | 73W-411H New Germany Recloser | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-08-30 | 2019-05-01 | 75446.72 | FIN Approval - Internal | 2019-10-31 |  | 3 | 80064.6628
51232-D842 | 51232 | #N/A | East Clifford Line Extension 73W | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2017-08-30 | 2019-09-30 | 49603.41 | FIN Approval - Internal | 2019-07-31 |  | 3 | 52639.5355
41350-D782 | 41350 | #N/A | 16W-301 Hebron Rebuild Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-08-31 |  | 102464.38 |  |  |  | 3 | 108736.0198
49868-D829 | 49868 | #N/A | 2017 Hydraulic Recloser Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-08-31 | 2020-02-01 | 241817.56 | FIN Approval - Internal | 2019-10-23 |  | 3 | 256618.7292
51477-D850 | 51477 | #N/A | 23H-301Forest Hill Dr and Tremont | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-09-28 | 2019-05-01 | 79420.68 | FIN Approval - Internal | 2019-03-29 |  | 3 | 84281.861
51535-D866 | 51535 | #N/A | Kentville URD Replacement 2017 | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-09-29 | 2020-03-01 | 51637.51 | FIN Approval - Internal | 2019-02-11 |  | 3 | 54798.1387
49216-D748 | 49216 | #N/A | Kentville URD Replacement 2016 | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-09-30 | 2019-05-01 | 130982.76 | FIN Approval - Internal | 2019-03-29 |  | 3 | 138999.9528
50798-D815 | 50798 | #N/A | 2017 Vault Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-09-30 | 2019-02-28 | 66327.69 | FIN Approval - Internal | 2018-10-01 |  | 3 | 70387.4752
52014-D880 | 52014 | #N/A | 85S-402 Line Removal & Reconfigurat | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2017-09-30 | 2020-11-01 | 277797.6 | FIN Approval - Internal | 2020-06-17 |  | 3 | 294801.0355
50800-D851 | 50800 | #N/A | 1C-411 Reinsulate and Pole Replacem | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-10-31 |  | 978189.36 |  |  |  | 3 | 1038062.3743
51529-D879 | 51529 | #N/A | R371-041 Recloser Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-10-31 | 2020-03-01 | 15714.39 | FIN Approval - Internal | 2019-02-11 |  | 3 | 16676.2364
50936-D820 | 50936 | #N/A | 2017 Manhole Equipment Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-11-01 | 2019-05-01 | 163101.66 | FIN Approval - Internal | 2019-02-11 |  | 3 | 173084.7864
49899-D840 | 49899 | #N/A | 10H Halifax 4kV Conversion Year 4 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-11-30 |  | 245225.66 |  |  |  | 3 | 260235.4322
50073-D791 | 50073 | #N/A | 4S-332 Bernard Lind Drive Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-11-30 | 2020-11-01 | 345726.92 | FIN Approval - Internal | 2020-08-12 |  | 3 | 366888.1733
50692-D799 | 50692 | #N/A | 2017 Padmount Switch Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-11-30 | 2019-05-01 | 200247.5 | FIN Approval - Internal | 2019-02-11 |  | 3 | 212504.249
51522-D872 | 51522 | #N/A | 24C-442GB - 19C Canso Recloser Addi | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2017-11-30 | 2019-09-30 | 61113.33 | FIN Approval - Internal | 2019-07-31 |  | 3 | 64853.9547
C0004518 | C0004518 | #N/A | December 25, 2017 Level 3 Storm | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2017-12-25 | 2019-09-30 | 1801670.62 | FIN Approval - Internal | 2019-07-31 |  | 3 | 1911947.2753
49836-D787 | 49836 | #N/A | 11S-302 11S-401 Rebuild Coxheath | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-12-29 | 2020-08-01 | 774528.1 | FIN Approval - Internal | 2020-06-17 |  | 3 | 821935.4159
49866-D788 | 49866 | #N/A | 512N-Toney River Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-12-29 | 2019-12-31 | 453401.55 | FIN Approval - Internal | 2019-11-28 |  | 3 | 481153.3521
49591-D763 | 49591 | #N/A | 3S Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2017-12-31 |  | 581560.69 | FIN Approval - Internal | 2020-01-27 |  | 3 | 617156.8567
50812-D839 | 50812 | #N/A | 11S-301J Voltage Regulator Addition | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-12-31 | 2019-05-01 | 30067.57 | FIN Approval - Internal | 2019-02-11 |  | 3 | 31907.9458
51231-D843 | 51231 | #N/A | Install Regulators Clare - 93V-312 | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-12-31 | 2019-09-30 | 211454.1 | FIN Approval - Internal | 2019-07-31 |  | 3 | 224396.7826
51531-D881 | 51531 | #N/A | 57C-426 New Sectionalizer | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2017-12-31 | 2020-03-01 | 30895.25 | FIN Approval - Internal | 2019-07-31 |  | 3 | 32786.2865
51551-D859 | 51551 | #N/A | 2H-411-Cowie Hill UG System Replac | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-12-31 | 2019-05-01 | 64082.12 | FIN Approval - Internal | 2019-02-11 |  | 3 | 68004.4584
52195 | 52195 | #N/A | D-101H Feeder Exit Cable Replace | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2017-12-31 | 2020-11-01 | 81199.63 | FIN Approval - Internal | 2020-06-11 |  | 3 | 86169.697
C0002678 | C0002678 | #N/A | 586C-311 Marble Mountain Road Line | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2017-12-31 | 2019-02-28 | 20378.69 | FIN Approval - Internal | 2018-10-01 |  | 3 | 21626.0289
C0002679 | C0002679 | #N/A | 586C-311 Militia Point Road Line | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | posted to CPR | 2017-12-31 | 2019-09-30 | 55631 | FIN Approval - Internal | 2019-07-31 |  | 3 | 59036.0622
C0005438 | C0005438 | #N/A | Jan 4, 2018 Level 4 Storm Response | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2018-01-04 |  | 2628839.07 | FIN Approval - Internal | 2019-07-31 |  | 2 | 2735044.1684
47403-D760 | 47403 | #N/A | Load Research Sample Update | Metering | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-01-31 | 2020-08-01 | 418033.97 | FIN Approval - Internal | 2020-06-17 |  | 2 | 434922.5424
49799-D784 | 49799 | #N/A | 532N Elm Street Conversion Phase 1 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-01-31 | 2020-11-01 | 525501.43 | FIN Approval - Internal | 2020-06-17 |  | 2 | 546731.6878
49956-D831 | 49956 | #N/A | 505V Station Retirement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-01-31 | 2019-05-01 | 24027.89 | FIN Approval - Internal | 2019-02-11 |  | 2 | 24998.6168
C0002182 | C0002182 | #N/A | 92H-332 Sheldrake Lake Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-01-31 |  | 301959.18 | FIN Approval - Internal | 2019-02-11 |  | 2 | 314158.3309
C0001950 | C0001950 | #N/A | New Distribution Rights-of-Way Ph 3 | Vegetation Management | Distribution Plant - D | n |  | Normal | Special | in service | 2018-02-01 |  | 10288858.36 | FIN Approval - Internal | 2020-09-10 |  | 2 | 10704528.2377
49867-D789 | 49867 | #N/A | 55V-313-Berwick North Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-02-02 | 2020-05-01 | 417925.99 | FIN Approval - Internal | 2020-03-02 |  | 2 | 434810.2
46991-D628 | 46991 | #N/A | 55V-322 - Lovette Road | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-02-28 | 2019-09-30 | 215017.09 | FIN Approval - Internal | 2019-07-31 |  | 2 | 223703.7804
47769-D826 | 47769 | #N/A | 509V-301 Overcove Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-02-28 | 2020-11-01 | 360035.61 | FIN Approval - Internal | 2020-06-17 |  | 2 | 374581.0486
51492-D858 | 51492 | #N/A | 87W-312G Tilley Point Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-02-28 |  | 57834 | FIN Approval - Internal | 2019-04-29 |  | 2 | 60170.4936
51970-D878 | 51970 | #N/A | 58C-405 Margaree Forks Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-02-28 | 2020-05-01 | 199911.22 | FIN Approval - Internal | 2020-03-02 |  | 2 | 207987.6333
52012-D882 | 52012 | #N/A | Voltage Regulator Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-02-28 | 2020-05-01 | 68246.95 | FIN Approval - Internal | 2020-03-02 |  | 2 | 71004.1268
52271 | 52271 | #N/A | D-2018 Padmount Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-02-28 |  | 1571162.75 |  |  |  | 2 | 1634637.7251
C0002651 | C0002651 | #N/A | 56N-414 Targeted -Device Replacemen | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-02-28 |  | 105241.68 | FIN Approval - Internal | 2020-06-17 |  | 2 | 109493.4439
C0007543 | C0007543 | #N/A | March 13, 2018 Level 3 Storm | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2018-03-13 | 2020-11-01 | 2965868.89 | FIN Approval - Internal | 2020-06-11 |  | 2 | 3085689.9932
45550-D557 | 45550 | #N/A | Upgrade Port Hood Transfer Scheme | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2018-03-31 | 2019-07-31 | 69487.47 | FIN Approval - Internal | 2019-04-29 |  | 2 | 72294.7638
50737-D813 | 50737 | #N/A | 36N-201 - Boars Back Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-03-31 | 2019-04-01 | 329735.27 | FIN Approval - Internal | 2018-12-18 |  | 2 | 343056.5749
50935-D819 | 50935 | #N/A | 551C-301 - Little Liscomb Rd - Rebu | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-03-31 | 2019-04-01 | 140274.11 | FIN Approval - Internal | 2018-12-18 |  | 2 | 145941.184
51521-D857 | 51521 | #N/A | 3S-302-3S-308 Reconfigure | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-03-31 | 2020-05-01 | 362054.11 | FIN Approval - Internal | 2020-03-02 |  | 2 | 376681.096
51697-D860 | 51697 | #N/A | 2017 Pole-Top Transf. Animal Guard | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2018-03-31 | 2020-03-01 | 33404.08 | FIN Approval - Internal | 2019-07-31 |  | 2 | 34753.6048
51785-D862 | 51785 | #N/A | 2017 Guy Guard Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-03-31 | 2020-03-01 | 3196.12 | FIN Approval - Internal | 2019-07-31 |  | 2 | 3325.2432
52221 | 52221 | #N/A | 515S-311-Rebuild on Aliant poles | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-03-31 | 2020-11-01 | 225245.18 | FIN Approval - Internal | 2020-06-11 |  | 2 | 234345.0853
C0002658 | C0002658 | #N/A | Intellirupter Revitalization | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-03-31 |  | 548983.28 |  |  |  | 2 | 571162.2045
50693-D803 | 50693 | #N/A | 2017 Manhole Cover Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-04-30 | 2019-09-30 | 127588.01 | FIN Approval - Internal | 2019-07-31 |  | 2 | 132742.5656
51501-D867 | 51501 | #N/A | 77V-302 Digby to Marshalltown | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-04-30 |  | 399871.03 | FIN Approval - Internal | 2020-10-01 |  | 2 | 416025.8196
C0003804 | C0003804 | #N/A | 510W-211 Crescent Beach Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-04-30 |  | 69343.44 | FIN Approval - Internal | 2020-06-11 |  | 2 | 72144.915
C0004562 | C0004562 | #N/A | 62N-413 Sherbrook Road Repole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-04-30 |  | 107814.79 | FIN Approval - Internal | 2020-06-17 |  | 2 | 112170.5075
50735-D814 | 50735 | #N/A | 79V-401 - Windsor Deteriorated Pole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-05-31 | 2020-03-01 | 127155.29 | FIN Approval - Internal | 2019-12-18 |  | 2 | 132292.3637
51482-D852 | 51482 | #N/A | 67C-411H Mabou Harbor Crossing Reb. | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-05-31 | 2020-08-01 | 356613.06 | FIN Approval - Internal | 2020-01-27 |  | 2 | 371020.2276
51527 | 51527 | #N/A | 57S-401 Catalone New Downline | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2018-05-31 | 2019-09-30 | 58063.36 | FIN Approval - Internal | 2019-07-31 |  | 2 | 60409.1197
52192 | 52192 | #N/A | 54H-303 UG Rep Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-05-31 |  | 388517.35 | FIN Approval - Internal | 2020-11-16 |  | 2 | 404213.4509
C0004598 | C0004598 | #N/A | 20N-201 Charles St & Academy St | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-05-31 |  | 217076.17 | FIN Approval - Internal | 2020-03-16 |  | 2 | 225846.0473
C0006018 | C0006018 | #N/A | D-Single Phase Recloser Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-05-31 |  | 78044.61 | FIN Approval - Internal | 2020-10-01 |  | 2 | 81197.6122
47777-D705 | 47777 | #N/A | 70W-321 Wile Lake Road | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-06-30 | 2020-02-01 | 97955.5 | FIN Approval - Internal | 2019-12-18 |  | 2 | 101912.9022
51491-D853 | 51491 | #N/A | 622V-211 King St Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-06-30 |  | 246198.37 | FIN Approval - Internal | 2020-03-02 |  | 2 | 256144.7841
C0008798 | C0008798 | #N/A | D-11S-301K Seaview Drive Highway Sh | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-06-30 |  | 167711.05 | FIN Approval - Internal | 2020-10-01 |  | 2 | 174486.5764
49223-D765 | 49223 | #N/A | 81S-305 Water St Rebuild Glace Bay | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-07-31 | 2020-03-01 | 128757.75 | FIN Approval - Internal | 2019-12-18 |  | 2 | 133959.5631
51512 | 51512 | #N/A | D-89W-302G Crouses Settlement Phase | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-07-31 |  | 150938.59 | FIN Approval - Internal | 2020-10-22 |  | 2 | 157036.509
52207 | 52207 | #N/A | D-678H-211 McNab’s Island Replaceme | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-07-31 |  | 263144.9 | FIN Approval - Internal | 2020-11-16 |  | 2 | 273775.954
C0001798 | C0001798 | #N/A | D-Halifax 4kV Conversion Phase 5 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-07-31 | 2020-11-01 | 213179.35 | FIN Approval - Internal | 2020-08-12 |  | 2 | 221791.7957
C0003738 | C0003738 | #N/A | D-50V-401 Kentville River Crossing | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-07-31 |  | 264937.87 | FIN Approval - Internal | 2020-11-16 |  | 2 | 275641.3599
C0005318 | C0005318 | #N/A | D-15S-301 Target Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-07-31 |  | 86159.46 |  |  |  | 2 | 89640.3022
C0005938 | C0005938 | #N/A | D-2C-402 Install VR & Upgrade SD | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-07-31 | 2020-11-01 | 72664.78 | FIN Approval - Internal | 2020-08-12 |  | 2 | 75600.4371
C0007258 | C0007258 | #N/A | D-104H-421 Barrington St Automatic | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2018-07-31 | 2020-05-01 | 170424.55 | FIN Approval - Internal | 2020-02-06 |  | 2 | 177309.7018
C0007318 | C0007318 | #N/A | D-85S-401GBA Cabot Trail Road shift | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-07-31 |  | 78085.33 | FIN Approval - Internal | 2020-10-22 |  | 2 | 81239.9773
49898 | 49898 | #N/A | D-15N-202 Victoria St-Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-08-31 | 2020-11-01 | 388997.98 | FIN Approval - Internal | 2020-06-17 |  | 2 | 404713.4984
51291-D844 | 51291 | #N/A | 657V-211-Maxwell Place Padmount Rep | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-08-31 |  | 247095.27 |  |  |  | 2 | 257077.9189
51513-D874 | 51513 | #N/A | 695H-311-Alan St-Stepdown Removal | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-08-31 |  | 47890.71 |  |  |  | 2 | 49825.4947
51519-D875 | 51519 | #N/A | 15N-401/402 Willow Street Pole Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-08-31 | 2020-03-01 | 285357.21 | FIN Approval - Internal | 2019-12-18 |  | 2 | 296885.6413
52208 | 52208 | #N/A | D-3S Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-08-31 | 2020-03-01 | 540983.74 | FIN Approval - Internal | 2019-12-18 |  | 2 | 562839.4831
C0005898 | C0005898 | #N/A | D-709H-221 Lister Dr Replacements a | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-08-31 |  | 55701.68 | FIN Approval - Internal | 2020-02-06 |  | 2 | 57952.0279
14873-D005-756 | 14873 | #N/A | Sydney Reg. E. - Replace Deteriorat | Distribution Line | Distribution Plant - D | n |  | Routine | D005 REPLACE DETERIORATED PLANT ROU | in service | 2018-09-01 |  | 12664.71 |  |  |  | 2 | 13176.3643
48437-D711 | 48437 | #N/A | 36W-301 East Sable Road Line Extens | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 166894.26 |  |  |  | 2 | 173636.7881
48439-D712 | 48439 | #N/A | 76V-301G Grafton Rd Line Extension | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-09-01 | 2020-08-01 | 188715.73 | FIN Approval - Internal | 2020-03-25 |  | 2 | 196339.8455
48441-D856 | 48441 | #N/A | 23W-301 Clyde River Line Relocation | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 55047.32 | FIN Approval - Internal | 2020-11-26 |  | 2 | 57271.2317
49034-D737 | 49034 | #N/A | 530W-201 John's Cove Causeway Reins | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2018-09-01 |  | 93436.9 |  |  |  | 2 | 97211.7508
50612-D797 | 50612 | #N/A | 22W-312G Targeted Device Replacemen | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 187567.32 |  |  |  | 2 | 195145.0397
50672-D804 | 50672 | #N/A | 605V-211-Culloden Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-09-01 | 2019-09-30 | 112805.01 | FIN Approval - Internal | 2019-07-31 |  | 2 | 117362.3324
51014-D834 | 51014 | #N/A | 50W-412G Charleston Abandoned Line | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 153740.09 |  |  |  | 2 | 159951.1896
51414-D847 | 51414 | #N/A | 543C-211 Mauger Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 351987.34 |  |  |  | 2 | 366207.6285
51532-D868 | 51532 | #N/A | 13V-303 Lake Lemerchant Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 103817.11 |  |  |  | 2 | 108011.3212
51897-D871 | 51897 | #N/A | 544W-311 Mt Pleasant Stepdown Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 65404.19 | FIN Approval - Internal | 2020-11-16 |  | 2 | 68046.5193
C0003718 | C0003718 | #N/A | 36W-301G Sable River Br Crossing | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 72030.39 |  |  |  | 2 | 74940.4178
C0003959 | C0003959 | #N/A | D-2018 Manhole Equipment Replact | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-09-01 | 2020-11-01 | 22988.72 | FIN Approval - Internal | 2020-06-11 |  | 2 | 23917.4643
C0003978 | C0003978 | #N/A | D-2018 Padmount Switch Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-09-01 | 2020-11-01 | 166763.29 | FIN Approval - Internal | 2020-08-12 |  | 2 | 173500.5269
C0003979 | C0003979 | #N/A | 2018 Vault Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 157956.29 | FIN Approval - Internal | 2020-11-16 |  | 2 | 164337.7241
C0001802 | C0001802 | #N/A | D-54C-211 Queen Street Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2018-09-27 | 2020-05-01 | 953678.2 | FIN Approval - Internal | 2020-02-06 |  | 2 | 992206.7993
C0004638 | C0004638 | #N/A | D-126H-312 Marine Dr PH2- Insul | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-30 |  | 173249.86 | FIN Approval - Internal | 2020-03-02 |  | 2 | 180249.1543
C0005358 | C0005358 | #N/A | D-19W-311 Lighthouse Rte Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2018-09-30 |  | 59081.88 | FIN Approval - Internal | 2020-10-22 |  | 2 | 61468.788
C0005939 | C0005939 | #N/A | D-522C-301 514C-312 Ashdale Reconfi | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-30 |  | 33971.32 | FIN Approval - Internal | 2020-08-12 |  | 2 | 35343.7613
C0007239 | C0007239 | #N/A | D-513V-311 Dakin Park Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-30 |  | 75314.27 | FIN Approval - Internal | 2020-08-12 |  | 2 | 78356.9665
C0009018 | C0009018 | #N/A | 77V-302 Digby to Marshalltown Ph-2 | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-09-30 |  | 150645.03 | FIN Approval - Internal | 2020-08-12 |  | 2 | 156731.0892
49607 | 49607 | #N/A | D-100C-422G Reinsulate | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 104672.29 | FIN Approval - Internal | 2020-11-16 |  | 2 | 108901.0505
C0003958 | C0003958 | #N/A | D-2018 Manhole Cover Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 192528.8 | FIN Approval - Internal | 2020-11-16 |  | 2 | 200306.9635
C0005283 | C0005283 | #N/A | D-57W-401 D417-010 Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2018-10-01 |  | 7086.6 |  |  |  | 2 | 7372.8986
C0005819 | C0005819 | #N/A | D-126H-312 Marine Dr PH1- Insulator | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-10-01 | 2020-05-01 | 206059.19 | FIN Approval - Internal | 2020-03-16 |  | 2 | 214383.9813
C0005958 | C0005958 | #N/A | D-50-410GAA Arbuckle Road Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-10-01 | 2020-11-01 | 69540.85 | FIN Approval - Internal | 2020-08-12 |  | 2 | 72350.3003
C0005978 | C0005978 | #N/A | D-57S-401 Albert Bridge Crossing | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 191911.77 | FIN Approval - Internal | 2020-10-22 |  | 2 | 199665.0055
C0007278 | C0007278 | #N/A | D-658V-211-Cortland Crescent Rebuil | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 99096.92 |  |  |  | 2 | 103100.4356
C0007478 | C0007478 | #N/A | D-530W-201 Overton Stepdown Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-10-01 | 2020-11-01 | 146796.76 | FIN Approval - Internal | 2020-08-12 |  | 2 | 152727.3491
C0007499 | C0007499 | #N/A | D-70V-311HB-Port Lorne Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 272260.89 |  |  |  | 2 | 283260.23
C0007502 | C0007502 | #N/A | D-65V-302GA-Forest Glade Repole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 329089.85 | FIN Approval - Internal | 2020-10-01 |  | 2 | 342385.0799
C0008938 | C0008938 | #N/A | D-542W-311 Brooklyn Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-10-01 |  | 538796.91 |  |  |  | 2 | 560564.3052
50714-D805 | 50714 | #N/A | 102W-311G Surette Cross Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-31 |  | 567.12 |  |  |  | 2 | 590.0316
C0009898 | C0009898 | M08829 | D - 2C-402 Reinsulate | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-10-31 |  | 806222.05 | FIN Approval - Internal | 2020-09-10 |  | 2 | 838793.4208
C0003778 | C0003778 | #N/A | Birch Street Sub. New Minas 22V-321 | Distribution Line | Distribution Plant - D | n |  | Normal | D061-New Customers - Residential | in service | 2018-11-01 |  | 9223.31 |  |  |  | 2 | 9595.9317
C0014418 | C0014418 | #N/A | Nov 28, 2018 Level 3 Storm - Dist | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2018-11-01 |  | 993073.09 | FIN Approval - Internal | 2020-10-22 |  | 2 | 1033193.2428
C0014278 | C0014278 | #N/A | Nov 13, 2018 Level 3 Storm - Dist | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2018-11-12 | 2020-11-01 | 334944.9 | FIN Approval - Internal | 2020-06-11 |  | 2 | 348476.674
C0010040 | C0010040 | #N/A | 2019 New Distribution ROW Widening | Vegetation Management | Distribution Plant - D | n |  | Normal | Special | in service | 2018-11-30 |  | 10356561.25 | FIN Approval - Internal | 2020-11-26 |  | 2 | 10774966.3245
C0013278 | C0013278 | #N/A | D-102W Tusket Voltage Correction | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-11-30 |  | 6029.48 |  |  |  | 2 | 6273.071
45612-D551 | 45612 | #N/A | 6S Terrace St Feeder Exit Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-12-01 | 2020-02-01 | 99049.49 | FIN Approval - Internal | 2019-12-18 |  | 2 | 103051.0894
52267 | 52267 | #N/A | D-16W-302H-Brenton Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-12-13 |  | 344278.41 | FIN Approval - Internal | 2020-10-22 |  | 2 | 358187.2578
47152-D665 | 47152 | #N/A | 22C-404 Arichat to Legion Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-12-31 |  | 183267.33 |  |  |  | 2 | 190671.3301
52185 | 52185 | #N/A | D-50N-410 Rebuild Phase 2 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-12-31 |  | 823682.86 |  |  |  | 2 | 856959.6475
52186 | 52186 | #N/A | D-4S Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2018-12-31 |  | 218393.68 |  |  |  | 2 | 227216.7847
C0010698 | C0010698 | #N/A | D-85S-401 Cabot Trail Widening | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-12-31 |  | 77003.43 |  |  |  | 2 | 80114.3686
C0013001 | C0013001 | #N/A | D - 58C-405H Middle River Road | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2018-12-31 |  | 55924.13 |  |  |  | 2 | 58183.4649
C0013299 | C0013299 | #N/A | D-102W-312 Tour Des Buttes Way Rebu | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-12-31 |  | 13994.78 |  |  |  | 2 | 14560.1691
49276-D774 | 49276 | #N/A | Moose River Gold Mine | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | in service | 2019-01-01 |  | 2381.25 |  |  |  | 1 | 2428.875
C0015479 | C0015479 | #N/A | Jan 20 2019 Level 3 Storm Dx | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-01-01 |  | 196573.31 | FIN Approval - Internal | 2020-11-16 |  | 1 | 200504.7762
C0015547 | C0015547 | #N/A | Northeast Planned Deteriorated Repl | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-01 |  | 89090.5 |  |  |  | 1 | 90872.31
C0015548 | C0015548 | #N/A | Northeast Unplanned Deteriorated Re | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-01 |  | 39700.8 |  |  |  | 1 | 40494.816
C0015641 | C0015641 | #N/A | Jan 24 2019 L3 Storm Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | posted to CPR | 2019-01-24 | 2020-11-01 | 136026.86 | FIN Approval - Internal | 2020-06-11 |  | 1 | 138747.3972
52224 | 52224 | #N/A | D-532N Elm Street Conversion P2&3 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-01-31 |  | 859625.08 | FIN Approval - Internal | 2020-11-26 |  | 1 | 876817.5816
C0006319 | C0006319 | #N/A | D-2019 PCB Pole Top Transformer Rep | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-01-31 |  | 178094.24 |  |  |  | 1 | 181656.1248
C0015761 | C0015761 | #N/A | Cape Breton High Priority FI | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-31 |  | 754426.93 |  |  |  | 1 | 769515.4686
C0015762 | C0015762 | #N/A | Metro High Priority FI | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-31 |  | 835156.17 |  |  |  | 1 | 851859.2934
C0015764 | C0015764 | #N/A | West High Priority FI | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-31 |  | 675291.78 |  |  |  | 1 | 688797.6156
C0015779 | C0015779 | #N/A | Deteriorated Make Ready | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-01-31 |  | 615730.2 |  |  |  | 1 | 628044.804
C0018059 | C0018059 | M09207 | 58C-403 Rebuild Hwy 19 South West | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-01-31 |  | 1246543.78 |  |  |  | 1 | 1271474.6556
C0015738 | C0015738 | #N/A | D-126H-312 HWY 207 Lead Insulator | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-02-01 |  | 143379.96 |  |  |  | 1 | 146247.5592
C0016558 | C0016558 | #N/A | August 29 2019 L3 Storm Distributio | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-02-24 |  | 598578.15 | FIN Approval - Internal | 2020-11-16 |  | 1 | 610549.713
C0011208 | C0011208 | #N/A | D-2019 Padmount Replacement Program | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-02-28 |  | 1433658.07 |  |  |  | 1 | 1462331.2314
C0015499 | C0015499 | #N/A | D-78W-302 ICP | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2019-03-01 | 2020-11-01 | 146465.92 | FIN Approval - Internal | 2020-08-12 |  | 1 | 149395.2384
C0015680 | C0015680 | #N/A | 22N-402 North Tyndal Lane Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-04-01 |  | 154930.61 |  |  |  | 1 | 158029.2222
C0016018 | C0016018 | #N/A | D-36W-304 Jordan Falls Line Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2019-04-01 |  | 163732.02 |  |  |  | 1 | 167006.6604
C0017538 | C0017538 | #N/A | 102W-312 - Line Ext. Armstrong Lake | Distribution Line | Distribution Plant - D | n |  | Normal | D062-New Customers - Commercial | posted to CPR | 2019-04-18 | 2020-11-01 | 94633.58 | FIN Approval - Internal | 2020-08-12 |  | 1 | 96526.2516
48436-D710 | 48436 | #N/A | 25W-301 Upper Clyde Rd Relocation | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-04-30 |  | 34852.64 |  |  |  | 1 | 35549.6928
C0006938 | C0006938 | #N/A | D-50W-412GA Mill Village Build | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2019-04-30 |  | 212.85 |  |  |  | 1 | 217.107
C0014620 | C0014620 | #N/A | D-1C-411 MacSween Street Pole Reloc | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | posted to CPR | 2019-04-30 | 2020-11-01 | 178706.06 | FIN Approval - Internal | 2020-08-12 |  | 1 | 182280.1812
C0015800 | C0015800 | #N/A | 18V-413 ICP | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-04-30 |  | 151314.52 |  |  |  | 1 | 154340.8104
C0017498 | C0017498 | #N/A | D-108H-412 Burnside New Pole Mount | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2019-05-01 | 2020-11-01 | 76692.84 | FIN Approval - Internal | 2020-08-12 |  | 1 | 78226.6968
52306 | 52306 | #N/A | D-5N-301 - Masstown Road Rebuild Ph | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2019-05-31 | 2020-11-01 | 130761.2 | FIN Approval - Internal | 2020-08-12 |  | 1 | 133376.424
C0016938 | C0016938 | #N/A | 88W-322 -Move Line To Road -Arcadia | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2019-05-31 |  | 103476.86 |  |  |  | 1 | 105546.3972
C0018299 | C0018299 | #N/A | 67C-411G - Holly's Hill re-Insulate | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-06-01 |  | 37833.07 |  |  |  | 1 | 38589.7314
C0018561 | C0018561 | #N/A | 85S-401- Cape Smokey TIR | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2019-06-01 |  | 378596.1 |  |  |  | 1 | 386168.022
44749-D527 | 44749 | #N/A | 509V-301 Tower and Crossing Replace | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-06-30 |  | 2177651.93 |  |  |  | 1 | 2221204.9686
51499 | 51499 | #N/A | 2018 Downline Recloser Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-06-30 |  | 290287.63 |  |  |  | 1 | 296093.3826
51500 | 51500 | #N/A | D-2018 Pin Insulator Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2019-06-30 | 2020-11-01 | 321249.24 | FIN Approval - Internal | 2020-08-12 |  | 1 | 327674.2248
51744 | 51744 | #N/A | D-30N-411 Maccan River Crossing Reb | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-06-30 |  | 748395.81 |  |  |  | 1 | 763363.7262
C0011207 | C0011207 | #N/A | D-15N Feeder Exit Cable Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2019-06-30 | 2020-11-01 | 153851.81 | FIN Approval - Internal | 2020-08-12 |  | 1 | 156928.8462
C0013418 | C0013418 | #N/A | D - 545W-311 Italy Cross Stepdown | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2019-06-30 |  | 177584.65 |  |  |  | 1 | 181136.343
47124-D635 | 47124 | #N/A | Advanced Meter Infrastructure | Advanced Meter Infrastructure | Distribution Plant - D | n |  | Normal | Special | in service | 2019-07-31 |  | 130642815.91 |  |  |  | 1 | 133255672.2282
52194 | 52194 | #N/A | D-6S-223-Harold Street Conversion | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-07-31 |  | 727381.79 |  |  |  | 1 | 741929.4258
52265 | 52265 | #N/A | 55V-322-English Mt Rd Reconfig | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-07-31 |  | 160697.24 |  |  |  | 1 | 163911.1848
C0021622 | C0021622 | #N/A | 103H-434 Protection Upgrades | Distribution Line | Distribution Plant - D | n |  | Normal | D051 - System Perf. Improvement | in service | 2019-08-16 |  | 122951.21 |  |  |  | 1 | 125410.2342
C0015359 | C0015359 | #N/A | 104S-313 Line Extension Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-09-01 |  | 842221.62 |  |  |  | 1 | 859066.0524
C0022323 | C0022323 | #N/A | Sep 2019 Hurricane Dorian - Distrib | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-09-01 |  | 23090678.5 |  |  |  | 1 | 23552492.07
43218-D757 | 43218 | #N/A | 88W-323A Tusket Islands Phase 3 | Distribution Line | Distribution Plant - D | n |  | Normal | Special | posted to CPR | 2019-09-30 | 2020-11-01 | 703298.91 | FIN Approval - Internal | 2020-08-12 |  | 1 | 717364.8882
51400 | 51400 | #N/A | D-2018 Substation Recloser Replacem | Substation Operations | Distribution Plant - D | n |  | Normal | Special | in service | 2019-09-30 |  | 475374.55 |  |  |  | 1 | 484882.041
C0018600 | C0018600 | #N/A | 648H-311 Logan Rd Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-10-01 |  | 105127.73 |  |  |  | 1 | 107230.2846
C0023263 | C0023263 | #N/A | Oct 17, 2019 L3 Storm -Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-10-17 |  | 651368.01 | FIN Approval - Internal | 2020-11-16 |  | 1 | 664395.3702
C0018240 | C0018240 | #N/A | 81S-301 - Donkin Haul Rd TIR | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2019-10-30 |  | 93604.82 |  |  |  | 1 | 95476.9164
C0019439 | C0019439 | #N/A | 1N-402 Marshland Dr. 3-Phase Extens | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2019-10-30 |  | 128371.34 |  |  |  | 1 | 130938.7668
C0015763 | C0015763 | #N/A | Northeast High Priority FI | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-10-31 |  | 1143507.5 |  |  |  | 1 | 1166377.65
C0011209 | C0011209 | #N/A | D-85S-401 Cabot Trail Rebuild | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-11-30 |  | 1531210.93 |  |  |  | 1 | 1561835.1486
C0015545 | C0015545 | #N/A | D-1H, 2H and 104H Inline Switches R | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-11-30 |  | 155939.46 |  |  |  | 1 | 159058.2492
C0018058 | C0018058 | #N/A | 36V-302G Ross Creek Rd Repole | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-11-30 |  | 68860.95 |  |  |  | 1 | 70238.169
C0019240 | C0019240 | #N/A | 1H-427 QEII Transformer Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-11-30 |  | 138578.88 |  |  |  | 1 | 141350.4576
C0024704 | C0024704 | #N/A | December 2019 Storm #2 Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-12-01 |  | 161065.32 |  |  |  | 1 | 164286.6264
C0024722 | C0024722 | #N/A | Feb 6, 2020 Storm-Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2019-12-25 |  | 4099336.56 |  |  |  | 1 | 4181323.2912
43195-D476 | 43195 | #N/A | 2013 Remote Communication on Reclos | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-12-31 |  | 89790.02 |  |  |  | 1 | 91585.8204
C0019579 | C0019579 | #N/A | 7N-301 ICP | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2019-12-31 |  | 156128.3 |  |  |  | 1 | 159250.866
C0023803 | C0023803 | #N/A | Landfills Conductors & Insulators | Distribution Line | Distribution Plant - D | n |  | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-01-01 |  | 374644.01 |  |  |  | 0 | 374644.01
C0024642 | C0024642 | #N/A | December 9, 2019 Storm-Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2020-01-01 |  | 46421.88 |  |  |  | 0 | 46421.88
C0026242 | C0026242 | #N/A | Padmount Square Primary Bushing | Distribution Line | Distribution Plant - D | n | replacement of bushings boots/inserts | Normal | D051 - System Perf. Improvement | in service | 2020-01-02 |  | 169.08 |  |  |  | 0 | 169.08
C0028102 | C0028102 | #N/A | 2020 Padmount Switch Replacement | Distribution Line | Distribution Plant - D | n | deteriorated plant | Normal | D055-Identified Deteriorated Plant | in service | 2020-02-01 |  | 44876.81 |  |  |  | 0 | 44876.81
C0016183 | C0016183 | #N/A | D-2020 Downline PCB Replacements | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2020-02-29 |  | 518394.67 |  |  |  | 0 | 518394.67
C0018400 | C0018400 | #N/A | Canada Post Auto-transfer Scheme | Distribution Line | Distribution Plant - D | n |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-02-29 |  | 18517.08 |  |  |  | 0 | 18517.08
C0020623 | C0020623 | #N/A | New Distribution ROW Phase 5 | Vegetation Management | Distribution Plant - D | n |  | Normal | Special | in service | 2020-02-29 |  | 6312150.51 |  |  |  | 0 | 6312150.51
C0025457 | C0025457 | #N/A | 20W-311 Willet Rd Repole | Distribution Line | Distribution Plant - D | n | Poles only - no conductor | Normal | D055-Identified Deteriorated Plant | in service | 2020-02-29 |  | 162690 |  |  |  | 0 | 162690
C0027223 | C0027223 | #N/A | 67C-412 Whycocomagh Roundabout | Distribution Line | Distribution Plant - D | n | Relocating poles | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-03-01 |  | 242339.67 |  |  |  | 0 | 242339.67
47775 | 47775 | #N/A | D-67C/58C Inverness Transfer Scheme | Distribution Line | Distribution Plant - D | n | Replacement of sectionalizers | Normal | Special | in service | 2020-03-30 |  | 223595.54 |  |  |  | 0 | 223595.54
C0017138 | C0017138 | #N/A | Feeders 1H-405 and 1H-431 Protectio | Substation Operations | Distribution Plant - D | n |  | Normal | Special | in service | 2020-03-30 |  | 91440.17 |  |  |  | 0 | 91440.17
C0020835 | C0020835 | #N/A | 2020 Padmount Replcement Program | Distribution Line | Distribution Plant - D | n | Like for Like replacements at end of life | Normal | Special | in service | 2020-03-31 |  | 1367533.8 |  |  |  | 0 | 1367533.8
C0026683 | C0026683 | #N/A | T&D Reliability Enhancements | Customer Reliability | Distribution Plant - D | n | Asset replacement, poles/framing/guys/ins. | Normal | Special | in service | 2020-03-31 |  | 538075.07 |  |  |  | 0 | 538075.07
C0028182 | C0028182 | #N/A | 4N-311 Targeted Asset Replacements | Customer Reliability | Distribution Plant - D | n | 50m Neutral, guys, insulators, cutouts, etc | Normal | Special | in service | 2020-04-21 |  | 27684.39 |  |  |  | 0 | 27684.39
C0026763 | C0026763 | #N/A | Town of Canso - Meter Installs | Metering | Distribution Plant - D | n |  | Normal | Special | in service | 2020-04-30 |  | 198708.22 |  |  |  | 0 | 198708.22
C0028804 | C0028804 | #N/A | 20H-301 Targeted Asset Replacements | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-05-01 |  | 58086.41 |  |  |  | 0 | 58086.41
C0028982 | C0028982 | #N/A | 104H-411 412 422 423 Targeted Asset | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-05-31 |  | 16238.4 |  |  |  | 0 | 16238.4
C0028803 | C0028803 | #N/A | 139H-414 Targeted Asset Replacement | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-06-02 |  | 25224.15 |  |  |  | 0 | 25224.15
C0013978 | C0013978 | #N/A | 11S Keltic Dr Substation Animal | Substation Operations | Distribution Plant - D | n | Install animal guards | Normal | Special | in service | 2020-06-30 |  | 77420.41 |  |  |  | 0 | 77420.41
C0028564 | C0028564 | #N/A | 92H-331 Targeted Asset Replacements | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-06-30 |  | 27170.77 |  |  |  | 0 | 27170.77
C0029699 | C0029699 | #N/A | 88W-312 Targeted Asset Replacements | Distribution Line | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-06-30 |  | 18959.21 |  |  |  | 0 | 18959.21
C0029742 | C0029742 | #N/A | 77V-401/509V-301 Targeted Asset Rep | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-06-30 |  | 24927.15 |  |  |  | 0 | 24927.15
C0030464 | C0030464 | #N/A | 100C-421 and 422 Targeted Asset Rep | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-07-01 |  | 29685.18 |  |  |  | 0 | 29685.18
C0029322 | C0029322 | #N/A | 1N-405H Salmon River Crossing Rebui | Distribution Line | Distribution Plant - D | n | Deteriorated plant - crossing removed | Normal | D055-Identified Deteriorated Plant | in service | 2020-07-31 |  | 19203.18 |  |  |  | 0 | 19203.18
C0029722 | C0029722 | #N/A | Herring Cove Rd Rebuild/Relocate | Distribution Line | Distribution Plant - D | n | Poles relocated due to HRM work | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-07-31 |  | 67807.77 |  |  |  | 0 | 67807.77
C0030486 | C0030486 | #N/A | 3S - Targeted Asset Replacements | Customer Reliability | Distribution Plant - D | n | pole hardware, guys | Normal | Special | in service | 2020-07-31 |  | 20057.26 |  |  |  | 0 | 20057.26
C0030944 | C0030944 | #N/A | 1N-402 1N-405 - Targeted Asset Repl | Customer Reliability | Distribution Plant - D | n | pole hardware, guys, wire sleeves, damaged conductor | Normal | Special | in service | 2020-07-31 |  | 7707.97 |  |  |  | 0 | 7707.97
C0011197 | C0011197 | #N/A | 64N Lourdes Street Conversion Ph 1 | Distribution Line | Distribution Plant - D | n | Conversion of 4kV at end of life | Normal | Special | in service | 2020-08-31 |  | 455351.52 |  |  |  | 0 | 455351.52
C0018302 | C0018302 | #N/A | 84S-302 - Sydney Airport Transfer S | Distribution Line | Distribution Plant - D | n | New Recloser | Normal | D051 - System Perf. Improvement | in service | 2020-08-31 |  | 63546.49 |  |  |  | 0 | 63546.49
C0030743 | C0030743 | #N/A | 509V East Ferry Landslide Remediati | Distribution Line | Distribution Plant - D | n | Land remediation | Normal | Special | in service | 2020-08-31 |  | 489293.05 |  |  |  | 0 | 489293.05
C0015679 | C0015679 | #N/A | D-20H-301G Old Sambro Rd Pole Repla | Distribution Line | Distribution Plant - D | n | Pole replacement | Normal | D055-Identified Deteriorated Plant | in service | 2020-09-30 |  | 70714.57 |  |  |  | 0 | 70714.57
C0020831 | C0020831 | #N/A | 2020 Vault Upgrade | Distribution Line | Distribution Plant - D | n |  | Normal | Special | in service | 2020-09-30 |  | 83657.98 |  |  |  | 0 | 83657.98
C0024686 | C0024686 | #N/A | 78W-301GA Eastern Points Repole | Distribution Line | Distribution Plant - D | n | Pole replacements | Normal | D005 REPLACE DETERIORATED PLANT ROU | in service | 2020-09-30 |  | 63385.41 |  |  |  | 0 | 63385.41
C0030444 | C0030444 | #N/A | D- 568C-311 Nelson Bridge Replace | Distribution Line | Distribution Plant - D | n | River crossing rebuild | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-09-30 |  | 4015.24 |  |  |  | 0 | 4015.24
C0030627 | C0030627 | #N/A | 88H-402 Protection Upgrades | Distribution Line | Distribution Plant - D | n | New reclosers and trip-savers | Normal | Special | in service | 2020-09-30 |  | 55836.39 |  |  |  | 0 | 55836.39
C0032827 | C0032827 | #N/A | Hurricane Teddy - Distribution | Distribution Line | Distribution Plant - D | n |  | Normal | D008-STORM COSTS ROUTINE | in service | 2020-09-30 |  | 534919.41 |  |  |  | 0 | 534919.41
C0017578 | C0017578 | #N/A | AMO TripSaver Pilot | AMO - Customer Operations | Distribution Plant - D | n | Install 25 trip-saver II units | Normal |  | in service | 2020-10-31 |  | 121909.13 |  |  |  | 0 | 121909.13
C0031148 | C0031148 | #N/A | Metro-Stack insulator replacements | Customer Reliability | Distribution Plant - D | n | Replace 700 insulators | Normal | Special | in service | 2020-10-31 |  | 79589.98 |  |  |  | 0 | 79589.98
C0032944 | C0032944 | #N/A | 85S-401- Abandoned RoW Removals | Distribution Line | Distribution Plant - D | n | Remove 58 offroad poles | Normal | D055-Identified Deteriorated Plant | in service | 2020-10-31 |  | 9689.14 |  |  |  | 0 | 9689.14
C0033405 | C0033405 | #N/A | 500 Mic Mac Blvd -Relocation | Distribution Line | Distribution Plant - D | n | Customer funded | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-10-31 |  | 110.23 |  |  |  | 0 | 110.23
C0015198 | C0015198 | M09209 | 50V Kentville Aluminum Light Pole R | Distribution Line | Distribution Plant - D | n | Deteriorated plant | Normal | Special | in service | 2020-11-30 |  | 200520.82 |  |  |  | 0 | 200520.82
C0029103 | C0029103 | #N/A | 58C-403 – Highway 219 Protection Up | Distribution Line | Distribution Plant - D | n | Install new recloser | Normal | D051 - System Perf. Improvement | in service | 2020-11-30 |  | 3629.73 |  |  |  | 0 | 3629.73
C0029162 | C0029162 | #N/A | 67C-411 Brook Village Protection | Distribution Line | Distribution Plant - D | n | Install new recloser | Normal | D051 - System Perf. Improvement | in service | 2020-11-30 |  | 7931.89 |  |  |  | 0 | 7931.89
C0029342 | C0029342 | #N/A | 67C-411/58C-403 Mabou and Dunvegan | Distribution Line | Distribution Plant - D | n | Install 4 trip-savers | Normal | D051 - System Perf. Improvement | in service | 2020-11-30 |  | 11233.38 |  |  |  | 0 | 11233.38
C0034166 | C0034166 | #N/A | 2859 ROBIE STREET RELOCATION | Distribution Line | Distribution Plant - D | n | Customer funded | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-11-30 |  | 629.98 |  |  |  | 0 | 629.98
52204 | 52204 | #N/A | 87W-312G-Tancook Island Replacement | Distribution Line | Distribution Plant - D | n | Deteriorated poles, cutouts, transformers | Normal | Special | in service | 2020-12-30 |  | 981441.69 |  |  |  | 0 | 981441.69
C0022163 | C0022163 | #N/A | 2020 Manhole Cover Replacement | Distribution Line | Distribution Plant - D | n |  | Normal | D055-Identified Deteriorated Plant | in service | 2020-12-31 |  | 119615.64 |  |  |  | 0 | 119615.64
C0027744 | C0027744 | #N/A | 3S-308-3S-405 - Reconfig and Remove | Distribution Line | Distribution Plant - D | n | removal of 1.7km of line | Normal | D055-Identified Deteriorated Plant | in service | 2020-12-31 |  | 8617.47 |  |  |  | 0 | 8617.47
C0031882 | C0031882 | #N/A | 22C-403-404 Feeder Exit Replacement | Distribution Line | Distribution Plant - D | n | Replacement of failed feeder exit | Normal | Special | in service | 2020-12-31 |  | 186095.12 |  |  |  | 0 | 186095.12
C0033424 | C0033424 | #N/A | 78W-301GA Eastern Points Repole | Distribution Line | Distribution Plant - D | n | Deteriorated poles, cutouts, transformers | Normal | Special | in service | 2020-12-31 |  | 275161.05 |  |  |  | 0 | 275161.05
C0025728 | C0025728 | #N/A | Bayers Road Development | Distribution Line | Distribution Plant - D | n | Relocate assets - no upgrades | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-02-01 |  | 314505.92 |  |  |  | 0 | 314505.92
C0028590 | C0028590 | #N/A | Windmill Rd and HWY 111 UG Crossing | Distribution Line | Distribution Plant - D | n | Deteriorated Plant - replacements | Normal | D055-Identified Deteriorated Plant | in service | 2020-05-01 |  | 181211.92 |  |  |  | 0 | 181211.92
C0030382 | C0030382 | #N/A | 22N-401 New Recloser Installation | Distribution Line | Distribution Plant - D | n | New recloser - reliability | Normal | D051 - System Perf. Improvement | in service | 2020-07-31 |  | 1898.57 |  |  |  | 0 | 1898.57
C0027645 | C0027645 | #N/A | D-4S-324-Tittle Bridge Reconfigure | Distribution Line | Distribution Plant - D | n | Line reconfiguration needed for bridge replacement | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-08-31 |  | 33421.86 |  |  |  | 0 | 33421.86
C0029242 | C0029242 | #N/A | 1N-421 Tidal Bore Rd Line Extension | Distribution Line | Distribution Plant - D | n | 1km new line and line removals due to Dyke Re-alignment | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-08-31 |  | 146143.57 |  |  |  | 0 | 146143.57
C0031224 | C0031224 | #N/A | 58C-405HA Middle River Reconfig | Distribution Line | Distribution Plant - D | n | NSTIR request to relocate utility crossing | Normal | D006 REGULATORY REPLACEMENTS | in service | 2020-11-01 |  | 17878.84 |  |  |  | 0 | 17878.84
C0029202 | C0029202 | #N/A | 4C-432 Beech Hill Rebuild | Distribution Line | Distribution Plant - D | n | Deteriorated plant - no conductor upgrade | Normal | D055-Identified Deteriorated Plant | in service | 2020-11-30 |  | 20206.63 |  |  |  | 0 | 20206.63
C0011200 | C0011200 | #N/A | D-6S-224 Birch Hill Drive Convers | Distribution Line | Distribution Plant - D | n | Conversion of 4kV at end of life | Normal | Special | in service | 2020-11-30 |  | 616911.3 |  |  |  | 0 | 616911.3
36942-T649 | 36942 | #N/A | 1H-B62 Bus Replacement Water St U&U |  | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-01-21 | 2014-08-08 | 1052046.04 | FIN Approval - Internal | 2014-08-08 |  | 9 | 1257292.4043
38818-T637 | 38818 | #N/A | Valley Protection Upgrades | Capital Projects Group | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-03-31 | 2019-11-28 | 247804.02 | FIN Approval - Internal | 2019-11-28 |  | 9 | 296148.7428
38856-T681 | 38856 | #N/A | L7011 Deteriorated Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-04-30 | 2017-06-23 | 1756235.87 | FIN Approval - Internal | 2017-06-23 |  | 9 | 2098864.437
39723-T652 | 39723 | #N/A | 104H-T63 Transformer Refurbishment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-05-20 | 2014-07-23 | 759692.52 | FIN Approval - Internal | 2014-07-23 |  | 9 | 907902.8851
38122-T684 | 38122 | #N/A | 2010 PCB Equip. Removal/Destruction |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-06-15 | 2014-08-01 | 1638107.45 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 1957690.0401
38266-T682 | 38266 | #N/A | 2010 Protection Upgrades | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-06-15 | 2017-06-27 | 419577.29 | FIN Approval - Internal | 2017-06-27 |  | 9 | 501433.7012
38857-T685 | 38857 | #N/A | L7004 Deteriorated Replacements |  | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-06-15 | 2014-08-08 | 2447746.17 | FIN Approval - Internal | 2014-08-08 |  | 9 | 2925283.2576
38878-T686 | 38878 | #N/A | 2010 Subs Cutout and Insul. Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-06-15 | 2017-06-23 | 484669.73 | FIN Approval - Internal | 2017-06-23 |  | 9 | 579225.1926
11004-T669 | 11004 | #N/A | Canaan Rd Circuit Breaker Additions |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-06-29 | 2014-08-01 | 2129493.04 | FIN Approval - Internal | 2014-08-08 |  | 9 | 2544941.307
38732-T650 | 38732 | #N/A | 1H Water St Replace 138 kV GIS | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-06-29 | 2016-01-31 | 8584762.19 | zINVALID FIN Approval - External | 2016-02-18 |  | 9 | 10259585.4967
40722-T655 | 40722 | #N/A | L5028 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-07-19 | 2014-11-21 | 283944.99 | FIN Approval - Internal | 2014-11-21 |  | 9 | 339340.5474
40726-T659 | 40726 | #N/A | L6513 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-07-19 | 2014-08-08 | 273421.82 | FIN Approval - Internal | 2014-08-08 |  | 9 | 326764.3852
38110-T701 | 38110 | #N/A | 2010 Tx Line Insulator Replacement | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-07-31 | 2017-06-23 | 1490348.72 | FIN Approval - Internal | 2017-06-23 |  | 9 | 1781104.6799
40280-T676 | 40280 | #N/A | 2011 Trans Switch & Breaker Upgrade | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-07-31 | 2013-07-16 | 3275924.7 | zINVALID FIN Approval - External | 2013-07-16 |  | 9 | 3915033.2643
40288-T690 | 40288 | #N/A | 2011 PCB Equipment Removals | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-08-08 | 2017-06-23 | 1805617.49 | FIN Approval - Internal | 2017-06-23 |  | 9 | 2157880.0441
40727-T660 | 40727 | #N/A | L7002 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-08-24 | 2015-04-30 | 271226.79 | FIN Approval - Internal | 2015-04-17 |  | 9 | 324141.1211
39626-T692 | 39626 | #N/A | Digby Wind Project Substation | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-09-28 | 2017-06-27 | 4332406.3 | FIN Approval - Internal | 2017-06-27 |  | 9 | 5177626.5734
39627-T693 | 39627 | #N/A | Digby Wind Project Trans Line |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-09-28 | 2014-07-22 | 4174697.88 | zINVALID FIN Approval - Internal | 2014-07-21 |  | 9 | 4989150.4126
39628-T694 | 39628 | #N/A | Digby Wind Project Interconnect | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2011-09-28 |  | 3988155.06 |  |  |  | 9 | 4766214.4747
40287-T654 | 40287 | #N/A | Substation Recloser Replacement | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-10-03 | 2016-01-31 | 4114179.9 | FIN Approval - External | 2016-02-18 |  | 9 | 4916825.8245
40728-T661 | 40728 | #N/A | L6515 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-10-03 | 2014-11-21 | 494165.46 | FIN Approval - Internal | 2014-11-21 |  | 9 | 590573.4689
40787-T664 | 40787 | #N/A | L5546 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-10-03 | 2012-10-30 | 85512.51 | zINVALID FIN Approval - External | 2012-09-27 |  | 9 | 102195.3652
40788-T665 | 40788 | #N/A | L6538 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-10-03 | 2014-08-08 | 177130.08 | FIN Approval - Internal | 2014-08-08 |  | 9 | 211686.8423
40790-T667 | 40790 | #N/A | Relocate L6511 and Feeder 4C-430 |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-10-03 | 2013-04-18 | -13069.37 | zINVALID FIN Approval - External | 2012-11-14 |  | 9 | -15619.107
40327-T695 | 40327 | #N/A | Glen Dhu 138 kV Substation | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-10-31 | 2019-12-31 | 3406923.82 | FIN Approval - Internal | 2019-11-18 |  | 9 | 4071589.3391
40270-T672 | 40270 | #N/A | Upgrade 69 kV Circuit to Bridge Ave | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2016-04-30 | 718294.04 | FIN Approval - Internal | 2016-04-18 |  | 9 | 858427.8693
40279-T663 | 40279 | #N/A | 2011 Pole Retreatment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-11-20 | 508208.1 | FIN Approval - Internal | 2014-11-20 |  | 9 | 607355.7236
40281-T668 | 40281 | #N/A | 2011 Tx Line Insulator Replacement |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-20 | 2013-10-22 | 3986553.24 | zINVALID FIN Approval - External | 2013-04-16 |  | 9 | 4764300.1515
40723-T656 | 40723 | #N/A | L6536 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2011-12-20 | 2013-11-14 | 191812.66 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 229233.8845
34262-T599 | 34262 | #N/A | Amherst Wind Farm |  | Transmission Plant - T | n |  | Normal | T004-TRANSMISSION SUBSTATION ADDITI | completed | 2011-12-31 | 2011-12-31 | 67521.09 |  |  |  | 9 | 80693.9529
34622-T670 | 34622 | #N/A | Upgrade L-8002 | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-12-31 | 2016-09-12 | 2377229.22 | FIN Approval - Internal | 2016-09-12 |  | 9 | 2841008.9747
38027-T700 | 38027 | #N/A | 2010 Trans Switch & Breaker Upgrade | Substation Operations | Transmission Plant - T | n |  | Normal |  | posted to CPR | 2011-12-31 | 2016-08-31 | 2059889.68 | FIN Approval - Internal | 2016-09-12 |  | 9 | 2461758.8487
38819-T675 | 38819 | #N/A | 51V Tremont Circuit Breaker & Bus | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2014-07-23 | 7437554.33 | FIN Approval - Internal | 2014-07-23 |  | 9 | 8888565.9085
40185-T653 | 40185 | #N/A | 104H-T61 Transformer Refurbishment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2014-08-20 | 882423.59 | FIN Approval - Internal | 2014-08-20 |  | 9 | 1054577.8748
40260-T689 | 40260 | #N/A | L7012 Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2016-12-14 | 1099112.2 | FIN Approval - External | 2016-12-14 |  | 9 | 1313540.8223
40285-T677 | 40285 | #N/A | 2011 Trans Subst Insulator & Cutout | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2016-01-31 | 878370.09 | FIN Approval - Internal | 2016-02-18 |  | 9 | 1049733.5671
40307-T673 | 40307 | #N/A | L6033 and L6035 Transmission Tower | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2019-02-28 | 837486.95 | FIN Approval - Internal | 2018-11-28 |  | 9 | 1000874.4303
40430-T648 | 40430 | #N/A | PH Biomass Tx Interconnection | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2019-06-30 | 1342899.03 | FIN Approval - Internal | 2019-03-25 |  | 9 | 1604888.6512
40883-T680 | 40883 | #N/A | NS-NB Interconnection | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2011-12-31 | 2020-04-01 | 250983.84 | FIN Approval - Internal | 2020-03-16 |  | 9 | 299948.922
41537-T706 | 41537 | #N/A | Amherst 138kV Substation | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2012-03-21 |  | 2718541.73 | FIN Approval - Internal | 2020-01-27 |  | 8 | 3185204.9206
42566-T714 | 42566 | #N/A | Upgrade L7001 |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-04-30 | 2014-07-11 | 196398.67 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 230112.3441
41005-T691 | 41005 | #N/A | Parrsboro Tidal Interconnection | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-05-18 | 2017-06-27 | 1728098.86 | FIN Approval - Internal | 2017-06-27 |  | 8 | 2024743.2406
42628-T717 | 42628 | #N/A | L5031 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-06-30 | 2016-08-31 | 151090.6 | FIN Approval - Internal | 2016-09-12 |  | 8 | 177026.7189
40266-T671 | 40266 | #N/A | L6002 Deteriorated Replacement 2012 | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-24 | 2020-03-01 | 1102189.41 | FIN Approval - Internal | 2020-02-28 |  | 8 | 1291390.5619
40724-T657 | 40724 | #N/A | L5532 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2014-07-23 | 137471.73 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 161070.0421
40725-T658 | 40725 | #N/A | L5011 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2014-07-23 | 154998.29 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 181605.2005
42626-T715 | 42626 | #N/A | Upgrade L7009 | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2016-01-31 | 585387.34 | FIN Approval - Internal | 2016-02-18 |  | 8 | 685874.5684
42629-T718 | 42629 | #N/A | L5575 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2014-07-23 | 95751.95 | FIN Approval - Internal | 2014-07-23 |  | 8 | 112188.6705
42632-T719 | 42632 | #N/A | L5530A Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2014-07-23 | 135746.11 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 159048.2032
42637-T724 | 42637 | #N/A | L6552 Upgrade |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-24 | 2014-07-11 | 284908.7 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 333815.9511
42758-T734 | 42758 | #N/A | 9W Tusket B52 Structure Replacement |  | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2012-09-24 | 2014-07-11 | 273013.32 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 319878.6175
43351-T743 | 43351 | #N/A | L5535 Upgrade |  | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | posted to CPR | 2012-09-24 | 2014-07-23 | 101271.27 | FIN Approval - Internal | 2014-07-23 |  | 8 | 118655.4335
40862-T696 | 40862 | #N/A | 101H-T61 Transformer Refurbishment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-25 | 2014-07-11 | 913124.52 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 1069870.9099
40867-T697 | 40867 | #N/A | 59C-T61 Transformer Refurbishment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-25 | 2014-08-01 | 898807.94 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 1053096.7546
42006-T702 | 42006 | #N/A | 7N Remote Grnd Electrode Connection |  | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2012-09-26 | 2014-07-24 | -41.86 | zINVALID FIN Approval - Internal | 2014-07-21 |  | 8 | -49.0457
41387-T710 | 41387 | #N/A | 2012 Transmission Line Insulator Re | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2016-01-31 | 3623427.83 | FIN Approval - Internal | 2016-02-18 |  | 8 | 4245423.2084
41399-T729 | 41399 | #N/A | 2012 Subst Insulator & Cutout Repla | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2017-06-23 | 431154.1 | FIN Approval - Internal | 2017-06-23 |  | 8 | 505165.7459
41426-T733 | 41426 | #N/A | 2012 Transmission Switch & Breaker | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2017-06-23 | 2122459.57 | FIN Approval - Internal | 2017-06-23 |  | 8 | 2486799.666
41429-T730 | 41429 | #N/A | 2012 Subst PCB Equipment Removal | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2016-12-14 | 1282336.85 | FIN Approval - External | 2016-12-14 |  | 8 | 1502461.9999
41430-T707 | 41430 | #N/A | 2012 Subst. Recloser Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-09-30 | 2017-06-23 | 1913554.62 | FIN Approval - Internal | 2017-06-23 |  | 8 | 2242034.2216
42633-T720 | 42633 | #N/A | L6005B Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-09-30 | 2016-08-31 | 304292.14 | FIN Approval - Internal | 2016-09-12 |  | 8 | 356526.7404
40868-T698 | 40868 | #N/A | 64V-T1 Transformer Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-10-19 | 2017-06-23 | 679938.19 | FIN Approval - External | 2017-06-23 |  | 8 | 796655.9588
43187-T742 | 43187 | #N/A | U&U L8002 Tower Refurbishment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-10-31 | 2016-08-31 | 276635.35 | FIN Approval - Internal | 2016-09-12 |  | 8 | 324122.4029
40233-T662 | 40233 | #N/A | 2011 Protection Upgrades TUC |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-11-01 | 2014-08-01 | 4173842.31 | FIN Approval - Internal | 2014-08-08 |  | 8 | 4890321.4973
41432-T713 | 41432 | #N/A | L7009 Lidar Upgrades & Maintenance | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-11-01 | 2020-05-01 | 3770099.38 | FIN Approval - Internal | 2020-04-21 |  | 8 | 4417272.3059
41386-T735 | 41386 | #N/A | 2012 Pole Retreatment |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-11-30 | 2014-08-20 | 540418.94 | zINVALID FIN Approval - Internal | 2014-08-20 |  | 8 | 633186.9207
41592-T732 | 41592 | #N/A | 88W New Recloser & Relocate 88W-322 |  | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2012-12-18 | 2014-11-20 | 135638.07 | zINVALID FIN Approval - Internal | 2014-11-20 |  | 8 | 158921.6171
42526-T711 | 42526 | #N/A | L6004 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2012-12-19 | 2016-04-30 | 179250.98 | FIN Approval - Internal | 2016-04-18 |  | 8 | 210021.0923
41535-T745 | 41535 | #N/A | 2012 Steel Tower Painting | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-01-01 | 2017-06-23 | 1701690.56 | FIN Approval - Internal | 2017-06-23 |  | 7 | 1954707.557
41550-T704 | 41550 | #N/A | Spare 30MVA 69KV 25/12KV Trans. | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-01-18 | 2017-06-27 | 523868.4 | FIN Approval - Internal | 2017-06-27 |  | 7 | 601760.1228
41844-T708 | 41844 | #N/A | L8004 & L7005 Reinsulate | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-01-31 | 2016-12-14 | 1016937.04 | FIN Approval - Internal | 2016-12-14 |  | 7 | 1168141.0027
39590-T725 | 39590 | #N/A | Upgrade L5547 |  | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-02-19 | 2014-07-23 | 93096.55 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 7 | 106938.6727
41391-T728 | 41391 | #N/A | L6025 Spar Arm Reinforcement | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-02-19 | 2014-07-23 | 834833.52 | FIN Approval - Internal | 2014-07-23 |  | 7 | 958961.2993
41536-T699 | 41536 | #N/A | 2012 Reliability Technology Trans. | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-03-27 | 2016-12-14 | 627061.69 | FIN Approval - Internal | 2016-12-14 |  | 7 | 720296.776
41348-T726 | 41348 | #N/A | 2012 Protection Upgrades Onslow | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-04-23 | 2015-01-28 | 2363221.76 | FIN Approval - Internal | 2015-01-28 |  | 7 | 2714598.9652
40323-T679 | 40323 | #N/A | Canaan Road Line Terminal | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-04-24 | 2016-09-12 | 979179.69 | FIN Approval - Internal | 2016-09-12 |  | 7 | 1124769.676
43323-T756 | 43323 | #N/A | Tuft's Cove Line Swap | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-04-27 | 2016-09-12 | 281415.91 | FIN Approval - Internal | 2016-09-12 |  | 7 | 323258.4225
44166-T764 | 44166 | #N/A | L6531 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-05-22 | 2014-07-23 | 108685.76 | FIN Approval - Internal | 2014-07-23 |  | 7 | 124845.7748
41517-T741 | 41517 | #N/A | L6535, 6536 & 6514 Upgrades | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-06-07 | 2016-09-12 | 2340820.35 | FIN Approval - Internal | 2016-09-12 |  | 7 | 2688866.7866
43226-T762 | 43226 | #N/A | 2013 Trans Switch & Breaker Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-06-26 | 2017-06-23 | 1774354.07 | FIN Approval - Internal | 2017-06-23 |  | 7 | 2038175.0895
43231-T758 | 43231 | #N/A | 2013 Substation PCB Equip Removal | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-06-26 | 2017-06-23 | 797063.07 | FIN Approval - External | 2017-06-23 |  | 7 | 915574.9247
43237-T763 | 43237 | #N/A | 2013 Substation Recloser Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-06-26 | 2016-12-14 | 1126614.24 | FIN Approval - External | 2016-12-14 |  | 7 | 1294125.6305
41390-T744 | 41390 | #N/A | 7V Methals Hydro Transformer Replac | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-07-31 | 2016-12-14 | 382465.8 | FIN Approval - Internal | 2016-12-14 |  | 7 | 439332.9828
40310-T747 | 40310 | #N/A | 15N Willow Ln Circuit Switcher Add | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2014-07-23 | 529153.95 | FIN Approval - Internal | 2014-07-23 |  | 7 | 607831.5583
43750-T760 | 43750 | #N/A | U&U 22W Barrington Passage | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2016-01-31 | 455031.48 | FIN Approval - Internal | 2016-02-18 |  | 7 | 522688.1394
43786-T768 | 43786 | #N/A | 2013 L8002 Tower Refurbishments | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-08-31 | 2017-06-26 | 2480929.31 | FIN Approval - Internal | 2017-06-26 |  | 7 | 2849807.9408
44315-T770 | 44315 | #N/A | L6002 Upgrade | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-08-31 | 2016-01-31 | 725241.78 | FIN Approval - Internal | 2016-02-18 |  | 7 | 833074.8383
41422-T736 | 41422 | #N/A | Onslow Spares Storage Upgrades | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-09-25 | 2016-08-31 | 379545.36 | FIN Approval - Internal | 2016-09-12 |  | 7 | 435978.3153
42627-T716 | 42627 | #N/A | L5004 Upgrade | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-09-25 | 2016-01-31 | 254635.77 | FIN Approval - Internal | 2016-02-18 |  | 7 | 292496.4595
42636-T723 | 42636 | #N/A | L6539 Upgrade | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-09-25 | 2014-07-23 | 225376.74 | FIN Approval - Internal | 2014-07-23 |  | 7 | 258887.0311
44363-T774 | 44363 | #N/A | U&U Replace 58H-T3 Transformer | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-09-25 | 2014-08-01 | 293325.22 | FIN Approval - Internal | 2014-08-08 |  | 7 | 336938.4762
40231-T688 | 40231 | #N/A | 2011 Protection Upgrades LAK | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-10-21 | 2014-08-01 | 1845085.77 | FIN Approval - Internal | 2014-08-08 |  | 7 | 2119423.5796
41434-T737 | 41434 | #N/A | Purchase New 42 MVA Spare Transform | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-10-28 | 2016-12-14 | 716220.74 | FIN Approval - External | 2016-12-14 |  | 7 | 822712.4989
41555-T738 | 41555 | #N/A | Spare Wind Farm Gen. Transformer | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-10-28 | 2019-05-01 | 776283.2 | FIN Approval - Internal | 2019-02-11 |  | 7 | 891705.3859
43488-T775 | 43488 | #N/A | 7H Substation Retirement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-10-28 | 2017-06-23 | 73861.56 | FIN Approval - Internal | 2017-06-23 |  | 7 | 84843.7154
44206-T766 | 44206 | #N/A | L5535 Upgrade - Part Of T011 | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-10-28 | 2017-06-23 | 182612.01 | FIN Approval - Internal | 2017-06-23 |  | 7 | 209763.7986
44228-T767 | 44228 | #N/A | L5026 Upgrade Pole & Arm Replacmnt | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-10-28 | 2014-07-23 | 101697.51 | FIN Approval - Internal | 2014-07-23 |  | 7 | 116818.4722
44314-T769 | 44314 | #N/A | L5003 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-10-28 | 2014-07-23 | 91619.98 | FIN Approval - Internal | 2014-07-23 |  | 7 | 105242.5579
44317-T772 | 44317 | #N/A | L7019 Upgrade | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-10-28 | 2016-08-31 | 135410.37 | FIN Approval - Internal | 2016-09-12 |  | 7 | 155543.9513
41589-T740 | 41589 | #N/A | 22N-Church St Replace 25 kV Bus | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-11-28 | 2016-01-31 | 803923.54 | FIN Approval - Internal | 2016-02-18 |  | 7 | 923455.4483
43606-T759 | 43606 | #N/A | L5549 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2013-11-28 | 2016-09-12 | 577375.68 | FIN Approval - Internal | 2016-09-12 |  | 7 | 663223.1685
44316-T771 | 44316 | #N/A | L6015 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-11-28 | 2014-07-23 | 124419.42 | FIN Approval - Internal | 2014-07-23 |  | 7 | 142918.8045
42635-T722 | 42635 | #N/A | L7012 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2013-12-18 | 2016-08-31 | 250065.5 | FIN Approval - Internal | 2016-09-12 |  | 7 | 287246.6558
33624-T639 | 33624 | #N/A | Spare Generator Transformer | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-01-30 | 2016-12-14 | 3520466.49 | FIN Approval - External | 2016-12-14 |  | 6 | 3964617.0593
44974-T799 | 44974 | #N/A | 2014 PCB Equipment Removals | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-02-01 | 2017-06-23 | 1262145.86 | FIN Approval - Internal | 2017-06-23 |  | 6 | 1421381.2352
44980-T798 | 44980 | #N/A | 2014 Trans. Switch & Breaker Rplcmn | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-02-01 | 2017-06-23 | 1322173.32 | FIN Approval - Internal | 2017-06-23 |  | 6 | 1488981.9047
44973-T803 | 44973 | #N/A | 2014 Subst Recloser Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-03-13 | 2017-06-23 | 442020.17 | FIN Approval - Internal | 2017-06-23 |  | 6 | 497786.504
41437-T739 | 41437 | #N/A | 104H-T62 Kempt Rd Transf Rewind | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-03-21 | 2017-06-23 | 1151315.99 | FIN Approval - External | 2017-06-23 |  | 6 | 1296568.8006
43222-T761 | 43222 | #N/A | 2013 Subst. Insulator and Cut-Outs | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-03-21 | 2017-06-23 | 235583.46 | FIN Approval - Internal | 2017-06-23 |  | 6 | 265305.2393
43293-T755 | 43293 | #N/A | Brushy Hill Protect Upgrade (138KV) | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-04-04 | 2016-02-28 | 2650781.44 | FIN Approval - Internal | 2016-02-23 |  | 6 | 2985210.4394
42634-T721 | 42634 | #N/A | L7003 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2014-06-23 | 2016-01-31 | 91653.76 | FIN Approval - Internal | 2016-02-18 |  | 6 | 103217.0201
43205-T808 | 43205 | #N/A | L5510 Insulator Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-06-30 | 2017-06-29 | 2908944.23 | FIN Approval - External | 2017-06-29 |  | 6 | 3275943.6716
43292-T754 | 43292 | #N/A | 120H-Brushy Hill BPS Upgrades 230KV | Trans - New | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-09-30 | 2016-02-28 | 1680583.65 | FIN Approval - Internal | 2016-02-23 |  | 6 | 1892610.1491
45797-T817 | 45797 | #N/A | L7004 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2014-09-30 | 2017-06-23 | 523137.52 | FIN Approval - Internal | 2017-06-23 |  | 6 | 589137.8151
43681-T788 | 43681 | #N/A | South Canoe Subs. Network Upgrades | Wind Generation - South Canoe | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-10-17 | 2019-04-01 | 4270257.6 | FIN Approval - External | 2019-01-03 |  | 6 | 4809003.6297
44975-T806 | 44975 | #N/A | Sacrificial Anode Installation Ph 1 | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-10-23 | 2017-01-16 | 784409.1 | FIN Approval - Internal | 2017-01-16 |  | 6 | 883372.0497
40789-T666 | 40789 | #N/A | Upgrade L7005 | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2014-10-29 | 2017-01-17 | 305021.65 | FIN Approval - Internal | 2017-01-17 |  | 6 | 343503.9193
41551-T748 | 41551 | #N/A | Glentosh Subst. Footing Remediation | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-10-29 | 2017-06-27 | 455177.83 | FIN Approval - Internal | 2017-06-27 |  | 6 | 512604.1662
43683-T789 | 43683 | #N/A | South Canoe Wind Project Tx Line | Wind Generation - South Canoe | Transmission Plant - T | n |  | Normal | Special | in service | 2014-10-31 |  | 5179766.65 | FIN Approval - External | 2019-01-18 |  | 6 | 5833258.5418
43675-T794 | 43675 | #N/A | Transmission Interconnection Sable | Wind Generation - Sable | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-11-24 | 2017-06-29 | 478660.11 | FIN Approval - Internal | 2017-06-29 |  | 6 | 539049.0275
43674-T793 | 43674 | #N/A | Sable Wind Network Upgrades | Wind Generation - Sable | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-11-28 | 2017-06-29 | 835040.36 | FIN Approval - Internal | 2017-06-29 |  | 6 | 940391.072
43676-T795 | 43676 | #N/A | Interconnection Substation Sable | Wind Generation - Sable | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-11-28 | 2017-06-29 | 1208366.32 | FIN Approval - Internal | 2017-07-24 |  | 6 | 1360816.7383
46771-T823 | 46771 | #N/A | Sable Wind Collector System | Wind Generation - Sable | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-12-15 | 2020-04-01 | 1085295.48 | FIN Approval - Internal | 2020-03-16 |  | 6 | 1222218.9834
44990-T796 | 44990 | #N/A | 104S Switch Replacement & Addition | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2014-12-31 | 2016-12-14 | 115602.71 | FIN Approval - Internal | 2016-12-14 |  | 6 | 130187.4276
45796-T815 | 45796 | #N/A | L6516 Upgrade | Trans - Replace / Refurb | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-01-08 | 2016-08-31 | 493256.93 | FIN Approval - Internal | 2016-09-12 |  | 5 | 544595.5075
43487-T785 | 43487 | #N/A | Add Breaker Backup at 81V and 12V | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-01-31 | 2017-01-17 | 119223.28 | FIN Approval - Internal | 2017-01-17 |  | 5 | 131632.1347
44984-T821 | 44984 | #N/A | 9C Aberdeen Line Tap | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-01-31 | 2019-05-01 | 831031.91 | FIN Approval - Internal | 2019-03-25 |  | 5 | 917526.3787
45793-T811 | 45793 | #N/A | L5028 Upgrade 2014 | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-01-31 | 2017-06-23 | 195188.76 | FIN Approval - Internal | 2017-06-23 |  | 5 | 215504.1629
46872-T829 | 46872 | #N/A | L6518 Replacement | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-01-31 | 2017-07-24 | 296981.06 | FIN Approval - Internal | 2017-07-24 |  | 5 | 327891.0873
43369-T783 | 43369 | #N/A | New Mobile Transformer 15MVA | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-02-28 | 2020-02-01 | 1840076.53 | FIN Approval - Internal | 2019-08-23 |  | 5 | 2031593.1732
43427-T776 | 43427 | #N/A | 62N-510 Breaker & Control Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-02-28 | 2017-01-16 | 515620.29 | FIN Approval - Internal | 2017-01-16 |  | 5 | 569286.4639
43489-T773 | 43489 | #N/A | 8H Substation Retirement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-02-28 | 2020-04-01 | 42507.92 | FIN Approval - Internal | 2020-03-25 |  | 5 | 46932.1785
46583-T826 | 46583 | #N/A | L6511 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-03-31 | 2017-07-24 | 783892.35 | FIN Approval - Internal | 2017-07-24 |  | 5 | 865480.4954
43684-T790 | 43684 | #N/A | Interconection Substation South Can | Wind Generation - South Canoe | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-04-30 | 2020-04-01 | 7981090.01 | FIN Approval - Internal | 2020-03-25 |  | 5 | 8811768.2687
46356-T841 | 46356 | #N/A | 2015 Sacrificial Anode Install Prog | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-04-30 | 2019-05-01 | 2378745.97 | FIN Approval - Internal | 2019-02-11 |  | 5 | 2626327.7612
44982-T797 | 44982 | #N/A | New Spare Transformer Replac 20W-T1 | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-05-31 | 2017-01-16 | 291873.68 | FIN Approval - Internal | 2017-01-16 |  | 5 | 322252.127
45792-T810 | 45792 | #N/A | L5012 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-06-30 | 2019-05-01 | 71268.14 | FIN Approval - Internal | 2019-03-25 |  | 5 | 78685.7853
46211-T816 | 46211 | #N/A | Upgrade L5502 | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-06-30 | 2017-07-24 | 141721.13 | FIN Approval - Internal | 2017-07-24 |  | 5 | 156471.579
46340-T833 | 46340 | #N/A | 2015 Switch & Breaker Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-06-30 | 2020-05-01 | 1505923.87 | FIN Approval - Internal | 2020-03-25 |  | 5 | 1662661.6359
47220-T861 | 47220 | #N/A | L5027A 9W, 20W and 22W | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-06-30 | 2017-07-24 | 68982.09 | FIN Approval - Internal | 2017-07-24 |  | 5 | 76161.8013
43672-T779 | 43672 | #N/A | 82V-T1 Transformer Rewind | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-08-31 | 2020-05-01 | 1756776.09 | FIN Approval - Internal | 2020-05-25 |  | 5 | 1939622.7565
47219-T851 | 47219 | #N/A | L7005 67N Onslow to 3C Port Hasting | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-08-31 | 2017-07-24 | 194841.38 | FIN Approval - Internal | 2017-07-24 |  | 5 | 215120.6273
44979-T836 | 44979 | #N/A | L5527 Structure Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-10-31 | 2020-08-01 | 756962.24 | FIN Approval - Internal | 2020-05-25 |  | 5 | 835747.4779
46335-T838 | 46335 | #N/A | L5511 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-10-31 | 2017-07-24 | 569221.84 | FIN Approval - Internal | 2017-07-24 |  | 5 | 628466.9063
47214-T845 | 47214 | #N/A | L5551 79W Lunenburg to 80W Indian P | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2015-10-31 | 2017-07-24 | 87764.58 | FIN Approval - Internal | 2017-07-24 |  | 5 | 96899.188
41438-T866 | 41438 | #N/A | 85S Cable Termination Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-11-30 | 2020-02-01 | 427630.1 | FIN Approval - Internal | 2019-08-23 |  | 5 | 472138.1843
44983-T809 | 44983 | #N/A | Reactor Bank Breaker Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2015-11-30 | 2017-07-24 | 415813.52 | FIN Approval - Internal | 2017-07-24 |  | 5 | 459091.7251
47191-T859 | 47191 | #N/A | L5536A 9W Tusket to 88W Pleasant St | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-01-31 | 2017-07-24 | 253888.4 | FIN Approval - Internal | 2017-07-24 |  | 4 | 274816.9692
47631-T865 | 47631 | #N/A | U&U Capacitor Bank Breaker Rpcmnts | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-01-31 | 2019-09-30 | 273736.64 | FIN Approval - Internal | 2019-07-31 |  | 4 | 296301.3425
48194-T868 | 48194 | #N/A | 88S-713 Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-01-31 | 2017-07-24 | 4467074.72 | FIN Approval - Internal | 2017-07-24 |  | 4 | 4835305.3381
43291-T786 | 43291 | #N/A | 67N-Onslow BPS Upgrades 230KV | Capital Projects Group | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-02-28 | 2018-08-31 | 3362634.16 | FIN Approval - Internal | 2018-06-28 |  | 4 | 3639823.3571
44985-T807 | 44985 | #N/A | Replace 230kV Kearney Disconnect Sw | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2016-02-29 |  | 352085.48 |  |  |  | 4 | 381108.6466
46333-T864 | 46333 | #N/A | L6538 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-02-29 | 2020-02-01 | 911299.45 | FIN Approval - Internal | 2020-02-28 |  | 4 | 986419.8321
46353-T834 | 46353 | #N/A | 2015 Substation Recloser Replacemen | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-02-29 | 2020-05-01 | 387388.87 | FIN Approval - Internal | 2020-03-25 |  | 4 | 419322.1713
47222-T853 | 47222 | #N/A | L5521 1N Onslow to 15N Willow Lane | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-02-29 | 2017-07-24 | 114739.16 | FIN Approval - Internal | 2017-07-24 |  | 4 | 124197.3568
44987-T820 | 44987 | #N/A | L7003 Lidar Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2016-03-31 |  | 10628779.02 |  |  |  | 4 | 11504932.2328
45794-T814 | 45794 | #N/A | L5040 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-03-31 | 2017-07-24 | 655354.98 | FIN Approval - Internal | 2017-07-24 |  | 4 | 709377.3066
46331-T837 | 46331 | #N/A | L7001 Replacements - Phase 2 | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-09-30 | 822290.77 | FIN Approval - Internal | 2019-07-31 |  | 4 | 890073.9743
46332-T863 | 46332 | #N/A | L6539 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2017-07-24 | 705259.85 | FIN Approval - Internal | 2017-07-24 |  | 4 | 763395.9428
46354-T839 | 46354 | #N/A | 2015 Reactor Breaker Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-05-01 | 522124.01 | FIN Approval - Internal | 2019-02-11 |  | 4 | 565163.8199
46582-T842 | 46582 | #N/A | L5569 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2020-03-01 | 149514.3 | FIN Approval - Internal | 2020-03-02 |  | 4 | 161839.0867
46586-T857 | 46586 | #N/A | 2015 PCB Removal - Substation | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-09-30 | 1476013.58 | FIN Approval - Internal | 2019-08-23 |  | 4 | 1597684.5676
47215-T846 | 47215 | #N/A | L6008 90H Sackville to 103H Lakesi | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-03-31 | 2019-12-31 | 375923.24 | FIN Approval - Internal | 2019-11-18 |  | 4 | 406911.4047
48113-T882 | 48113 | #N/A | 2016 Steel Tower Refurbishment | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-05-01 | 1940802 | FIN Approval - Internal | 2019-10-31 |  | 4 | 2100786.501
48597-T897 | 48597 | #N/A | L5530A Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-04-22 | 2020-08-01 | 215817.67 | FIN Approval - Internal | 2020-03-25 |  | 4 | 233607.9867
45033-T812 | 45033 | #N/A | L7001 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-04-30 | 2019-12-31 | 699595.97 | FIN Approval - Internal | 2019-11-28 |  | 4 | 757265.1769
46337-T840 | 46337 | #N/A | L6535/L6551 Insulator Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-04-30 | 2017-07-24 | 377198.53 | FIN Approval - Internal | 2017-07-24 |  | 4 | 408291.8196
48066-T880 | 48066 | #N/A | 2016 PCB Removal - Substation | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-04-30 | 2020-03-01 | 3526302.04 | FIN Approval - Internal | 2020-03-02 |  | 4 | 3816982.734
48604-T909 | 48604 | #N/A | L5538 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-05-30 | 2017-07-24 | 175269.23 | FIN Approval - Internal | 2017-07-24 |  | 4 | 189717.0512
48114-T893 | 48114 | #N/A | 2016 Steel Tower Life Extension | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-05-31 | 2019-05-01 | 1519276.91 | FIN Approval - Internal | 2019-03-29 |  | 4 | 1644514.1873
48593-T895 | 48593 | #N/A | L5016 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-06-30 | 2020-02-01 | 165791.63 | FIN Approval - Internal | 2019-12-18 |  | 4 | 179458.1922
48598-T898 | 48598 | #N/A | L5530B Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-06-30 | 2017-07-24 | 167327.48 | FIN Approval - Internal | 2017-07-24 |  | 4 | 181120.6456
48599-T899 | 48599 | #N/A | L5054 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-06-30 | 2020-04-01 | 53176.18 | FIN Approval - Internal | 2020-03-25 |  | 4 | 57559.6074
48602-T901 | 48602 | #N/A | L5047 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-06-30 | 2020-08-01 | 81451.52 | FIN Approval - Internal | 2020-03-25 |  | 4 | 88165.7447
48059-T877 | 48059 | #N/A | 2016 Switch and Breaker Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-07-31 | 2020-02-01 | 1178178.59 | FIN Approval - Internal | 2019-08-23 |  | 4 | 1275298.396
47212-T844 | 47212 | #N/A | L5506 55N Pictou to 54N Abercrombie | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-08-04 | 2019-12-31 | 339770.86 | FIN Approval - Internal | 2019-11-28 |  | 4 | 367778.9059
48116-T883 | 48116 | #N/A | 2016 Sacrificial Anode Installation | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-08-04 | 2020-02-01 | 1198819.71 | FIN Approval - Internal | 2019-08-23 |  | 4 | 1297641.0081
43490-T860 | 43490 | #N/A | Steel Tower Life Ext - Hali Harbour | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2016-08-31 |  | 833760.61 | FIN Approval - External | 2019-09-06 |  | 4 | 902489.298
45651-T792 | 45651 | #N/A | L8004 Upgrade | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-08-31 | 2020-03-01 | 125986.98 | FIN Approval - Internal | 2019-12-18 |  | 4 | 136372.3589
47221-T852 | 47221 | #N/A | L5015 Avon to Three Mile Plains | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-08-31 | 2017-07-24 | 40267.97 | FIN Approval - Internal | 2017-07-24 |  | 4 | 43587.3457
47949-T876 | 47949 | #N/A | L5028 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2016-08-31 |  | 891792.35 |  |  |  | 4 | 965304.7197
47952-T869 | 47952 | #N/A | L7001 Replacements (Phase 3 & 4) | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-08-31 | 2019-12-31 | 1509306.56 | FIN Approval - Internal | 2019-11-28 |  | 4 | 1633721.9598
49052-T908 | 49052 | #N/A | L5506 Pictou Roundabout Line | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-08-31 | 2020-04-01 | 88052.53 | FIN Approval - Internal | 2020-03-16 |  | 4 | 95310.8902
49373-T912 | 49373 | #N/A | L5544 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-08-31 | 2019-12-31 | 92319.48 | FIN Approval - Internal | 2019-11-28 |  | 4 | 99929.5741
49505-T920 | 49505 | #N/A | L5011 Line Relocation | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-08-31 | 2020-02-01 | 17060.42 | FIN Approval - Internal | 2019-12-18 |  | 4 | 18466.7473
47914-T874 | 47914 | #N/A | L6537 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2016-09-02 |  | 1552221.58 |  |  |  | 4 | 1680174.5576
46513-T827 | 46513 | #N/A | 3C Port Hastings BPS Upgrade | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-09-12 | 2019-04-01 | 3315242.44 | FIN Approval - External | 2018-08-15 |  | 4 | 3588525.0353
44976-T832 | 44976 | #N/A | 10H 25kV Breaker Rplcmnt & Reconfig | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-09-21 | 2020-02-01 | 1157139.93 | FIN Approval - Internal | 2019-08-23 |  | 4 | 1252525.4739
43260-T746 | 43260 | #N/A | 2013 Trans Line Insulator Replace | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-09-30 | 2019-04-01 | 303626.16 | FIN Approval - External | 2019-01-25 |  | 4 | 328654.7202
48062-T878 | 48062 | #N/A | 2016 Reactor Breaker Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2016-09-30 |  | 582317.47 |  |  |  | 4 | 630319.1569
49378-T916 | 49378 | #N/A | L6517 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-09-30 | 2017-07-24 | 379099.55 | FIN Approval - Internal | 2017-07-24 |  | 4 | 410349.5448
49380-T918 | 49380 | #N/A | L6545 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-10-28 | 2020-05-01 | 56670.85 | FIN Approval - Internal | 2020-03-25 |  | 4 | 61342.3506
43261-T831 | 43261 | #N/A | 6V-GT1 Hollow Bridge Hydro Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-10-31 | 2020-05-01 | 533267.75 | FIN Approval - Internal | 2020-03-25 |  | 4 | 577226.1625
43266-T887 | 43266 | #N/A | 89S Point Aconi ST2 Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-10-31 | 2020-05-01 | 1524240.2 | FIN Approval - Internal | 2020-03-25 |  | 4 | 1649886.612
47912-T873 | 47912 | #N/A | L6552 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-10-31 | 2020-02-01 | 947929.95 | FIN Approval - Internal | 2019-07-31 |  | 4 | 1026069.8633
48112-T906 | 48112 | #N/A | 11W King Street Substation Ret | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-10-31 | 2020-04-01 | 72516.42 | FIN Approval - Internal | 2020-03-25 |  | 4 | 78494.1051
48595-T896 | 48595 | #N/A | L5548 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2016-12-09 | 2020-05-01 | 242889.91 | FIN Approval - Internal | 2020-03-25 |  | 4 | 262911.8499
44977-T813 | 44977 | #N/A | 3W Breaker, Switch & Cable Rplacmen | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-12-31 | 2019-09-30 | 645757.56 | FIN Approval - Internal | 2019-08-23 |  | 4 | 698988.7505
46397-T855 | 46397 | #N/A | Substation Telemetry | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-12-31 | 2020-05-01 | 204833.29 | FIN Approval - Internal | 2020-03-02 |  | 4 | 221718.1405
48151-T903 | 48151 | #N/A | 2016 Insulator Replacement Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2016-12-31 | 2020-04-01 | 150611.68 | FIN Approval - Internal | 2020-03-25 |  | 4 | 163026.9261
49992-T938 | 49992 | #N/A | 2017 Transmission ROW Widening | Vegetation Management | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-01-01 | 2020-11-01 | 5494422.68 | FIN Approval - Internal | 2020-06-11 |  | 3 | 5830725.3034
48026-T921 | 48026 | #N/A | L-6033/L-6035 CT Ratio Changes 1H | MDRR Transmission | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-01-10 | 2019-07-31 | 9098.09 | FIN Approval - Internal | 2019-07-16 |  | 3 | 9654.9659
49775-T927 | 49775 | #N/A | L5004 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-02-01 |  | 969140.03 |  |  |  | 3 | 1028459.153
49815-T929 | 49815 | #N/A | 2017 Steel Tower Refurbishment | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-02-28 |  | 1912767.11 |  |  |  | 3 | 2029843.7593
47935-T875 | 47935 | #N/A | L5040 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-12-31 | 1107608.74 | FIN Approval - Internal | 2019-11-28 |  | 3 | 1175403.2558
49813-T926 | 49813 | #N/A | 2017 Sacrificial Anode Installation | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2020-11-01 | 1749976.89 | FIN Approval - Internal | 2020-06-17 |  | 3 | 1857089.4755
49878-T937 | 49878 | #N/A | 2017 Substation Insulator Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-03-31 | 2020-05-01 | 353314.79 | FIN Approval - Internal | 2020-05-25 |  | 3 | 374940.4817
49838-T924 | 49838 | #N/A | 2017 Substation PCB Equip Rplcmnt | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2017-04-30 |  | 4339739.59 |  |  |  | 3 | 4605366.3708
49792-T934 | 49792 | #N/A | 2017 Line Retirement Program | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-06-01 | 2020-11-01 | 544381.87 | FIN Approval - Internal | 2020-08-12 |  | 3 | 577702.3955
49793-T946 | 49793 | #N/A | L7011 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-06-01 |  | 4595800.53 |  |  |  | 3 | 4877100.2888
49814-T948 | 49814 | #N/A | 2017 Steel Tower Life Extension | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-06-01 | 2020-11-01 | 1643870.96 | FIN Approval - Internal | 2020-08-12 |  | 3 | 1744489.0137
51118-T953 | 51118 | #N/A | L5549 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-06-23 | 2020-11-01 | 279661.3 | FIN Approval - Internal | 2020-06-17 |  | 3 | 296778.8089
46339-T825 | 46339 | #N/A | 120H Replace SVC Controls | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-06-30 | 2020-01-01 | 10027941.28 | FIN Approval - Internal | 2020-02-06 |  | 3 | 10641731.5099
49789-T925 | 49789 | #N/A | L6515 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-06-30 | 2020-08-01 | 2590653.46 | FIN Approval - Internal | 2020-03-25 |  | 3 | 2749222.177
49798-T935 | 49798 | #N/A | 2017 Capacitor Bank Breaker Replace | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-06-30 | 2020-11-01 | 209820.49 | FIN Approval - Internal | 2020-06-17 |  | 3 | 222663.1826
45795-T862 | 45795 | #N/A | L6503 Replacements | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2019-09-30 | 825251.14 | FIN Approval - Internal | 2019-07-31 |  | 3 | 875763.1118
47956-T932 | 47956 | #N/A | L7004 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2020-11-01 | 481722.61 | FIN Approval - Internal | 2020-08-12 |  | 3 | 511207.8875
48067-T892 | 48067 | #N/A | 2016 Oil Containment Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2020-08-01 | 351498.95 | FIN Approval - Internal | 2020-08-12 |  | 3 | 373013.4977
51404-T970 | 51404 | #N/A | 2018/2019 Steel Tower Life Extensio | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-07-31 | 2021-01-01 | 2992783.11 | FIN Approval - Internal | 2020-10-01 |  | 3 | 3175965.3786
47954-T963 | 47954 | #N/A | L7012 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-08-01 |  | 4396365.39 |  |  |  | 3 | 4665458.1228
49376-T915 | 49376 | #N/A | L6011 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2017-08-11 |  | 75385.34 |  |  |  | 3 | 79999.5259
47217-T847 | 47217 | #N/A | L6012 17V St. Croix to 43V Cannan | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-08-30 | 2020-02-01 | 352174.89 | FIN Approval - Internal | 2019-12-18 |  | 3 | 373730.8107
51696-T964 | 51696 | #N/A | L7015 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-08-30 | 2020-02-01 | 400214.81 | FIN Approval - Internal | 2019-12-18 |  | 3 | 424711.1581
47218-T848 | 47218 | #N/A | L5563 2S VJ to 4STownsend St | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-08-31 | 2020-11-01 | 216079.99 | FIN Approval - Internal | 2020-06-17 |  | 3 | 229305.814
47950-T881 | 47950 | #N/A | L-5017 Replacements & Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-08-31 |  | 2853689.88 |  |  |  | 3 | 3028358.5302
49381-T919 | 49381 | #N/A | L7014 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-08-31 | 2020-02-01 | 304954.38 | FIN Approval - Internal | 2019-12-18 |  | 3 | 323620.0277
49776-T933 | 49776 | #N/A | L7008 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-08-31 |  | 733883.93 |  |  |  | 3 | 778803.4976
49778-T957 | 49778 | #N/A | L5535 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-09-28 |  | 2290953.45 |  |  |  | 3 | 2431178.1288
49375-T914 | 49375 | #N/A | L6003 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-09-29 | 2020-05-01 | 254587.16 | FIN Approval - Internal | 2020-05-25 |  | 3 | 270169.9309
49928-T949 | 49928 | #N/A | 3S Gannon Rd. Bus Reconfiguration | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2017-10-01 |  | 834622.78 |  |  |  | 3 | 885708.3711
46757-T867 | 46757 | #N/A | 88S Lingan 230kV BPS Upgrades | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-10-23 | 2020-05-01 | 3296759.76 | FIN Approval - Internal | 2020-02-24 |  | 3 | 3498547.8314
49929-T945 | 49929 | #N/A | Tap Changer Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2017-10-31 |  | 519552.81 |  |  |  | 3 | 551353.5984
49948-T960 | 49948 | #N/A | 2017/2018 Isolated Structure Replac | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-11-01 |  | 2529228.79 |  |  |  | 3 | 2684037.8258
51092-T947 | 51092 | #N/A | L5011 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-11-13 | 2020-11-01 | 351271.54 | FIN Approval - Internal | 2020-06-17 |  | 3 | 372772.1684
49374-T913 | 49374 | #N/A | L6002 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-11-18 | 2020-02-01 | 96089.92 | FIN Approval - Internal | 2019-12-18 |  | 3 | 101971.3918
44981-T871 | 44981 | #N/A | 2C Port Hastings Tx Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-11-30 | 2020-05-01 | 2006133.93 | FIN Approval - Internal | 2020-02-28 |  | 3 | 2128925.3756
48591-T894 | 48591 | #N/A | L5003 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-11-30 | 2020-11-01 | 103296.81 | FIN Approval - Internal | 2020-05-25 |  | 3 | 109619.4011
49379-T917 | 49379 | #N/A | L6527 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-11-30 | 2020-11-01 | 84560.4 | FIN Approval - Internal | 2020-05-25 |  | 3 | 89736.173
51901-T972 | 51901 | #N/A | L-6010 2017R Replacements and Upg | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-11-30 | 2020-02-01 | 139181.78 | FIN Approval - Internal | 2019-12-18 |  | 3 | 147700.8184
49782-T958 | 49782 | #N/A | L5027B Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2017-12-31 |  | 1532095.81 | FIN Approval - Internal | 2020-11-26 |  | 3 | 1625872.3303
49833-T936 | 49833 | #N/A | 2017 Oil Containment Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2017-12-31 | 2020-08-01 | 339359.52 | FIN Approval - Internal | 2020-08-12 |  | 3 | 360131.0375
51096-T942 | 51096 | #N/A | L-5019 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2017-12-31 | 2020-03-01 | 159521.62 | FIN Approval - Internal | 2020-03-02 |  | 3 | 169285.6193
45066-T802 | 45066 | #N/A | Upgrade L6511 and L7019 | Maritime Link Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2018-01-15 |  | 2691016.62 |  |  |  | 2 | 2799733.6914
45067-T801 | 45067 | #N/A | 67N Onslow 345 KV Node Swap | Maritime Link Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2018-01-15 |  | 2982713.69 |  |  |  | 2 | 3103215.3231
49818-T923 | 49818 | #N/A | 2017/2018 Tx Switch & Breaker Rplmt | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2018-01-31 |  | 1045370.9 |  |  |  | 2 | 1087603.8844
51111-T950 | 51111 | #N/A | L5037 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-01-31 |  | 369170.98 | FIN Approval - Internal | 2020-10-01 |  | 2 | 384085.4876
51969 | 51969 | #N/A | 2018 Transmission ROW Widening 69kV | Vegetation Management | Transmission Plant - T | n |  | Normal | Special | in service | 2018-02-20 |  | 5542106.33 | FIN Approval - Internal | 2020-10-22 |  | 2 | 5766007.4257
48063-T879 | 48063 | #N/A | 2016 Capacitor Bank Breaker Repl. | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-03-31 | 2020-05-01 | 253153.88 | FIN Approval - Internal | 2020-02-06 |  | 2 | 263381.2968
51402-T969 | 51402 | #N/A | 2018/2019 Sacrificial Anode Install | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-04-30 |  | 3073174.01 |  |  |  | 2 | 3197330.24
51403 | 51403 | #N/A | T-2018 PCB Removal Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2018-04-30 |  | 3408583.54 |  |  |  | 2 | 3546290.315
51935-T976 | 51935 | #N/A | L-5555 2017R Replacements and Upg. | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-04-30 |  | 452593.65 |  |  |  | 2 | 470878.4335
49774-T956 | 49774 | #N/A | L5527 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-05-31 |  | 1784759.13 | FIN Approval - Internal | 2020-11-26 |  | 2 | 1856863.3989
49795-T941 | 49795 | #N/A | 100C Cape Porcupine Switch Addition | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-05-31 | 2021-01-01 | 248377.98 | FIN Approval - Internal | 2020-10-01 |  | 2 | 258412.4504
52102 | 52102 | #N/A | L5014-2018 Replacements and Upgr | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-05-31 |  | 1039350.04 |  |  |  | 2 | 1081339.7816
49922-T939 | 49922 | #N/A | Western Switching Upgrades | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-06-30 | 2021-01-01 | 650673.92 | FIN Approval - Internal | 2020-10-01 |  | 2 | 676961.1464
51405 | 51405 | #N/A | 2018 Wood Pole Retreatment Program | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-06-30 |  | 924520.55 |  |  |  | 2 | 961871.1802
52305 | 52305 | #N/A | 2018 Substation Insulator Replc | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2018-06-30 |  | 206787.29 |  |  |  | 2 | 215141.4965
C0007538 | C0007538 | #N/A | 87S-GT3 Pipe Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2018-06-30 |  | 33301.55 |  |  |  | 2 | 34646.9326
43324-T782 | 43324 | #N/A | L6513 Rebuild/upgrade line terminal | Maritime Link Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2018-07-05 |  | 18627164.15 |  |  |  | 2 | 19379701.5817
43678-T800 | 43678 | #N/A | Separate L8004/L7005 | Maritime Link Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2018-07-20 |  | 20385511.05 |  |  |  | 2 | 21209085.6964
48156-T904 | 48156 | #N/A | East Switch Upgrades 58C | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-07-31 | 2020-08-01 | 63436.08 | FIN Approval - Internal | 2020-08-12 |  | 2 | 65998.8976
51119-T954 | 51119 | #N/A | L5550 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2018-07-31 | 2020-08-01 | 187358.89 | FIN Approval - Internal | 2020-06-11 |  | 2 | 194928.1892
51917-T974 | 51917 | #N/A | L6515 2017R Replc and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2018-07-31 | 2020-11-01 | 51129.06 | FIN Approval - Internal | 2020-06-11 |  | 2 | 53194.674
52119 | 52119 | #N/A | L5054 2018 Replacements and Upgra | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-07-31 |  | 784720.25 | FIN Approval - Internal | 2020-11-26 |  | 2 | 816422.9481
C0009598 | C0009598 | #N/A | 100C-T61 Transformer Repair | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2018-07-31 | 2020-11-01 | 84789.32 | FIN Approval - Internal | 2020-10-01 |  | 2 | 88214.8085
47915-T931 | 47915 | #N/A | L5053 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-08-31 |  | 402184 |  |  |  | 2 | 418432.2336
51742-T966 | 51742 | #N/A | 88S-302 Metal Clad Switchgear Repl. | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2018-08-31 | 2020-05-01 | 310725.88 | FIN Approval - Internal | 2020-03-02 |  | 2 | 323279.2056
C0005040 | C0005040 | #N/A | T-2V-T41 Refurb and Support Str Rep | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2018-08-31 | 2020-11-01 | 165302.99 | FIN Approval - Internal | 2020-06-11 |  | 2 | 171981.2308
49371-T911 | 49371 | #N/A | L5039 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-09-01 |  | 192565.52 |  |  |  | 2 | 200345.167
51318-T961 | 51318 | #N/A | L-5055 - 98W-Rio Algom Tin Mine | Substation Operations | Transmission Plant - T | n |  | Normal | T004-TRANSMISSION SUBSTATION ADDITI | posted to CPR | 2018-09-01 | 2020-03-01 | 12793.63 | FIN Approval - Internal | 2020-03-02 |  | 2 | 13310.4927
51916-T973 | 51916 | #N/A | L-5003 2017R Replacements and Upgr. | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-09-01 |  | 178482.68 | FIN Approval - Internal | 2020-11-26 |  | 2 | 185693.3803
51932-T975 | 51932 | #N/A | L6533 2017R Replc and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | posted to CPR | 2018-09-01 | 2021-01-01 | 88204.48 | FIN Approval - Internal | 2020-11-26 |  | 2 | 91767.941
51974-T971 | 51974 | #N/A | Remote Substation Video/Thermal Mon | Substation Operations | Transmission Plant - T | n |  | Normal | T004-TRANSMISSION SUBSTATION ADDITI | in service | 2018-09-01 |  | 414451.14 |  |  |  | 2 | 431194.9661
46591-T828 | 46591 | #N/A | 88S Lingan Replace 230kV GIS | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2018-09-28 |  | 14858073.85 | FIN Approval - Internal | 2020-01-27 |  | 2 | 15458340.0335
48061-T884 | 48061 | #N/A | New Mobile Substation 7.5MVA | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2018-09-30 |  | 2534685.18 |  |  |  | 2 | 2637086.4613
51117-T944 | 51117 | #N/A | L5502 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-09-30 |  | 49607.81 |  |  |  | 2 | 51611.9655
51863 | 51863 | #N/A | 2018 Tap Changer Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-09-30 | 2021-01-01 | 417340.3 | FIN Approval - Internal | 2020-10-01 |  | 2 | 434200.8481
43200-T930 | 43200 | #N/A | 2017 Wood Pole Retreatment | Transmission Line | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-10-01 | 2018-10-01 | -0.01 |  |  |  | 2 | -0.010404
49779 | 49779 | #N/A | T-L6537 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-10-31 |  | 1942239.64 |  |  |  | 2 | 2020706.1215
49821-T940 | 49821 | #N/A | Mersey River Hydro Spare Transformr | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-10-31 | 2020-11-01 | 439279.61 | FIN Approval - Internal | 2020-06-17 |  | 2 | 457026.5062
51112-T951 | 51112 | #N/A | L5042 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2018-10-31 |  | 2343.19 |  |  |  | 2 | 2437.8549
52320 | 52320 | #N/A | L6549 2018 Replacements & Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-10-31 |  | 1454552.95 |  |  |  | 2 | 1513316.8892
C0014320 | C0014320 | #N/A | Nov 28, 2018 L3 Storm -Transmission | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | posted to CPR | 2018-11-01 | 2020-11-01 | 584914.05 | FIN Approval - Internal | 2020-06-17 |  | 2 | 608544.5776
C0013920 | C0013920 | #N/A | 2019 Substation Storm Replacements | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2018-11-13 | 2021-01-01 | 8963.64 | FIN Approval - Internal | 2020-10-01 |  | 2 | 9325.7711
52241 | 52241 | #N/A | 16V-T2 Weymouth Hydro Transformer R | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2018-11-30 | 2021-01-01 | 674829.15 | FIN Approval - Internal | 2020-10-01 |  | 2 | 702092.2477
51406 | 51406 | #N/A | 2018/2019 Transmission Switch & Bre | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2018-12-31 |  | 1036672.5 |  |  |  | 2 | 1078554.069
C0011243 | C0011243 | #N/A | T-L5551 -Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2018-12-31 |  | 943913.78 |  |  |  | 2 | 982047.8967
C0014158 | C0014158 | #N/A | T-L5548 Emergency Repairs | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | in service | 2018-12-31 |  | 966751.37 | FIN Approval - Internal | 2020-12-29 |  | 2 | 1005808.1253
C0010042 | C0010042 | #N/A | 2019 Transmission ROW Widening 69kV | Vegetation Management | Transmission Plant - T | n |  | Normal | Special | in service | 2019-01-01 |  | 5612430.54 |  |  |  | 1 | 5724679.1508
C0015480 | C0015480 | #N/A | Jan 20,2019 L3 Storm-Transmission | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | in service | 2019-01-20 |  | 2228.99 | FIN Approval - Internal | 2020-06-11 |  | 1 | 2273.5698
C0015640 | C0015640 | #N/A | Jan 24,2019 L3 Storm-Transmission | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | in service | 2019-01-20 |  | 32147.64 | FIN Approval - Internal | 2020-11-16 |  | 1 | 32790.5928
51398 | 51398 | #N/A | 2018/2019 Steel Tower Refurb | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-01-31 |  | 2035207.82 |  |  |  | 1 | 2075911.9764
51956 | 51956 | #N/A | 6P Mobile Substation Rewind | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-01-31 |  | 752627.93 |  |  |  | 1 | 767680.4886
C0011241 | C0011241 | #N/A | T-L5026 -Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-01-31 |  | 1374896.39 |  |  |  | 1 | 1402394.3178
C0013938 | C0013938 | #N/A | Lingan SF6 Bus Refurbishment | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-01-31 |  | 249072.59 | FIN Approval - Internal | 2020-11-26 |  | 1 | 254054.0418
C0011240 | C0011240 | #N/A | T-L5511 -Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-02-28 |  | 1485115.59 |  |  |  | 1 | 1514817.9018
C0011338 | C0011338 | #N/A | T-L5548- Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-04-30 |  | 1146339.74 |  |  |  | 1 | 1169266.5348
C0017198 | C0017198 | #N/A | 2019 Transmission LiDAR | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-04-30 |  | 672125.73 |  |  |  | 1 | 685568.2446
C0010952 | C0010952 | #N/A | 2019/20 Substation PCB Equip Replac | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-05-31 |  | 2413687.09 |  |  |  | 1 | 2461960.8318
C0010978 | C0010978 | #N/A | T-2019/2020 Tran Switch & Breaker R | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-05-31 |  | 643425.93 |  |  |  | 1 | 656294.4486
49777 | 49777 | #N/A | L7002 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-06-30 |  | 1171856.12 |  |  |  | 1 | 1195293.2424
52059 | 52059 | #N/A | L5039 - 2018 Replacements and Upgr | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-06-30 |  | 636638.83 |  |  |  | 1 | 649371.6066
C0020162 | C0020162 | #N/A | Substation Replacement of Grounds | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2019-07-01 |  | 502809.36 |  |  |  | 1 | 512865.5472
41439-T712 | 41439 | #N/A | 5P & 6P Mobile Substation Upgrades | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-07-15 |  | 468640.28 | FIN Approval - Internal | 2020-11-16 |  | 1 | 478013.0856
43267-T835 | 43267 | #N/A | 13V Gulch Replace 13V-GT1 & 13V-VR1 | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-07-31 |  | 1011935.78 |  |  |  | 1 | 1032174.4956
46366-T854 | 46366 | #N/A | 65V Middleton Substation RTU Add | Telecom | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2019-07-31 | 2020-11-01 | 190198.91 | FIN Approval - Internal | 2020-06-17 |  | 1 | 194002.8882
48111-T905 | 48111 | #N/A | East Switch Upgrades 15S | Substation Operations | Transmission Plant - T | n |  | Normal | Special | posted to CPR | 2019-07-31 | 2020-11-01 | 290264.84 | FIN Approval - Internal | 2020-06-17 |  | 1 | 296070.1368
49783 | 49783 | #N/A | L5027A Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-07-31 |  | 791304.92 |  |  |  | 1 | 807131.0184
49788 | 49788 | #N/A | L5564 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-07-31 |  | 780462.21 |  |  |  | 1 | 796071.4542
C0011851 | C0011851 | #N/A | T - 2019 Tap Changer Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-07-31 |  | 217888.45 |  |  |  | 1 | 222246.219
C0011339 | C0011339 | #N/A | T-L6549-Replacements and Upgr Ph2 | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-08-01 |  | 1620556.31 |  |  |  | 1 | 1652967.4362
47131-T858 | 47131 | #N/A | L8001 Structure 58 Replacement | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-08-30 |  | 828181.27 |  |  |  | 1 | 844744.8954
C0010949 | C0010949 | #N/A | T - 2019/2020 Steel Tower Life Ext | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-08-30 |  | 1446969.31 |  |  |  | 1 | 1475908.6962
51797 | 51797 | #N/A | 2018 Oil Containment Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-08-31 |  | 344911.36 |  |  |  | 1 | 351809.5872
C0014040 | C0014040 | #N/A | 89S-ST1-Neutral Grounding Resistor | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2019-09-01 |  | 11151.36 | FIN Approval - Internal | 2020-11-26 |  | 1 | 11374.3872
C0022342 | C0022342 | #N/A | Sep 2019 Hurricane Dorian - Substai | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2019-09-01 |  | 71675.37 | FIN Approval - Internal | 2020-11-16 |  | 1 | 73108.8774
C0022322 | C0022322 | #N/A | Sep 2019 - Hurricane Dorian - Trans | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | in service | 2019-09-06 |  | 504912.12 |  |  |  | 1 | 515010.3624
45053-T818 | 45053 | #N/A | 69Kv Structure Replacements West | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-09-30 |  | 225494.35 |  |  |  | 1 | 230004.237
48057-T965 | 48057 | #N/A | Replace 69kV cables between 2S& 83S | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-10-31 |  | 603587.4 |  |  |  | 1 | 615659.148
C0011300 | C0011300 | #N/A | T-L7005 -Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-10-31 |  | 1433125.11 |  |  |  | 1 | 1461787.6122
C0021105 | C0021105 | M09480 | L7002 Replacements and Upgrades PH1 | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-11-01 |  | 559783.03 |  |  |  | 1 | 570978.6906
C0020628 | C0020628 | #N/A | L6055 - Hwy 107 Monopoles TIR | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2019-11-30 |  | -0.23 |  |  |  | 1 | -0.2346
C0024724 | C0024724 | #N/A | Feb 6, 2020 L3 Storm Transmission | Transmission Line | Transmission Plant - T | n |  | Normal | T001-TRANSMISSION LINE REPLACEMENTS | in service | 2019-12-01 |  | 256882.02 |  |  |  | 1 | 262019.6604
52323 | 52323 | #N/A | 2C Port Hastings Uprated to NPCC BP | Capital Projects Group - Transmission | Transmission Plant - T | n |  | Normal | Special | in service | 2019-12-18 |  | 3984626.93 |  |  |  | 1 | 4064319.4686
C0013458 | C0013458 | #N/A | 10W Tusket 69kV Bus Bypass | Gas Turbine Generation | Transmission Plant - T | n |  | Normal | Special | in service | 2019-12-19 |  | 189100.84 |  |  |  | 1 | 192882.8568
43428-T787 | 43428 | #N/A | Remove 6S 4kV Switchgear Breakers | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2019-12-31 |  | 193091.94 |  |  |  | 1 | 196953.7788
C0010948 | C0010948 | #N/A | T-2019/2020 Sacrificial Anode Inst | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-12-31 |  | 640937.21 |  |  |  | 1 | 653755.9542
C0010950 | C0010950 | #N/A | T - 2019/2020 Steel Tower Refurb | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2019-12-31 |  | 1801928.99 |  |  |  | 1 | 1837967.5698
C0024867 | C0024867 | #N/A | 67N Leaking CT Replacement (T003) | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-01-01 |  | 30061.06 |  |  |  | 0 | 30061.06
C0024868 | C0024868 | #N/A | Battery Bank and Charger Replacemen | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-01-01 |  | 111821.62 |  |  |  | 0 | 111821.62
C0024870 | C0024870 | #N/A | 50N-GT5 Regasket and Radiator Repla | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-01-01 |  | 20314.92 |  |  |  | 0 | 20314.92
C0024872 | C0024872 | #N/A | Lingan New Coolers (T003) | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-01-01 |  | 17855.03 |  |  |  | 0 | 17855.03
C0025382 | C0025382 | #N/A | 2020 Unknown Additions (T004) | Substation Operations | Transmission Plant - T | n |  | Normal | T004-TRANSMISSION SUBSTATION ADDITI | in service | 2020-01-01 |  | 58417.61 |  |  |  | 0 | 58417.61
C0025383 | C0025383 | #N/A | 2020 Transformer Refurbishment | Substation Operations | Transmission Plant - T | n |  | Normal | T004-TRANSMISSION SUBSTATION ADDITI | in service | 2020-01-01 |  | 79990.11 |  |  |  | 0 | 79990.11
C0022283 | C0022283 | #N/A | 58C-T1 Margaree Failed Transformer | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-01-30 |  | 731771.15 |  |  |  | 0 | 731771.15
52285 | 52285 | #N/A | L5524 Replacements & Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2020-01-31 |  | 1665120.08 |  |  |  | 0 | 1665120.08
C0020627 | C0020627 | #N/A | 2020 Transmission ROW Widening 69kV | Vegetation Management | Transmission Plant - T | n |  | Normal | Special | in service | 2020-01-31 |  | 2184117.83 |  |  |  | 0 | 2184117.83
C0024875 | C0024875 | #N/A | 30W Deteriorated Bus Structure Repl | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-03-01 |  | 232149.6 |  |  |  | 0 | 232149.6
C0028464 | C0028464 | #N/A | 12V-T2 Tapchanger Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-04-23 |  | 180314.78 |  |  |  | 0 | 180314.78
C0021123 | C0021123 | #N/A | 2020/2021 Substation PCB Equipment | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-04-30 |  | 3813043.18 |  |  |  | 0 | 3813043.18
C0024486 | C0024486 | M09710 | 2S-T1 Transformer Replacement | Substation Operations | Transmission Plant - T | n | Failed unit | Normal | Special | in service | 2020-04-30 |  | 2689746.44 |  |  |  | 0 | 2689746.44
49790-T959 | 49790 | #N/A | L5505 Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2020-05-31 |  | 755352.19 |  |  |  | 0 | 755352.19
C0011242 | C0011242 | #N/A | T-L5541 -Replacements and Upgrades | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2020-06-30 |  | 1800710 |  |  |  | 0 | 1800710
C0010955 | C0010955 | #N/A | 2020/2021 Wood Pole Retreatment | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2020-07-31 |  | 478552.63 |  |  |  | 0 | 478552.63
C0030785 | C0030785 | #N/A | Wreck Cove oil reconditioning | Substation Operations | Transmission Plant - T | n |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-07-31 |  | 134708.98 |  |  |  | 0 | 134708.98
C0026102 | C0026102 | #N/A | 2020 Substation Theft Prevention | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-08-31 |  | 29211.89 |  |  |  | 0 | 29211.89
C0030263 | C0030263 | #N/A | L7003 & L7004 - Hwy 104 Twinning | Transmission Line | Transmission Plant - T | n |  | Normal | T011-Provincial Planned Trans Line | in service | 2020-08-31 |  | 72.89 |  |  |  | 0 | 72.89
C0030142 | C0030142 | #N/A | L6515, L6516 Structures Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-09-30 |  | 311357.24 |  |  |  | 0 | 311357.24
52238 | 52238 | #N/A | 2018/2019 Capacitor Bank Breaker Re | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-10-31 |  | 197582.06 |  |  |  | 0 | 197582.06
C0011850 | C0011850 | #N/A | T - 2019 Substation Insulator Repla | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-10-31 |  | 45702.55 |  |  |  | 0 | 45702.55
C0034209 | C0034209 | #N/A | 1C-GT2 Transformer Failure | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-10-31 |  | 1817888.66 |  |  |  | 0 | 1817888.66
48131 | 48131 | #N/A | 48H-T1 Replacement | Substation Operations | Transmission Plant - T | n | Deteriorated Plant - no capacity increase | Normal | Special | in service | 2020-11-30 |  | 1503974.01 |  |  |  | 0 | 1503974.01
52314 | 52314 | #N/A | 1C-GT1/UT1 Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-11-30 |  | 1505655.45 |  |  |  | 0 | 1505655.45
C0020743 | C0020743 | #N/A | Ragged Lake UPS Replacement | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-11-30 |  | 188372.57 |  |  |  | 0 | 188372.57
C0021130 | C0021130 | #N/A | 48H Metalclad Switchgear Replacemen | Substation Operations | Transmission Plant - T | n | Replaced with reclosers | Normal | Special | in service | 2020-11-30 |  | 1290193.38 |  |  |  | 0 | 1290193.38
C0032745 | C0032745 | #N/A | 89H Oil Spill Remediation | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-11-30 |  | 721759.38 |  |  |  | 0 | 721759.38
C0011918 | C0011918 | #N/A | T-2019 Oil Containment Program | Substation Operations | Transmission Plant - T | n |  | Normal | Special | in service | 2020-12-15 |  | 275152.65 |  |  |  | 0 | 275152.65
52317 | 52317 | #N/A | 2020 Line Retirement Program | Transmission Line | Transmission Plant - T | n |  | Normal | Special | in service | 2020-12-31 |  | 99478.42 |  |  |  | 0 | 99478.42
C0024862 | C0024862 | #N/A | 2020 Unplanned Failures (T003) | Substation Operations | Transmission Plant - T | n |  | Routine | T003-TRANSMISSION SUBSTATION REPLAC | in service | 2020-12-31 |  | 502555.88 |  |  |  | 0 | 502555.88
C0025384 | C0025384 | #N/A | 9W-517 & 529 Capbank Civil Work | Substation Operations | Transmission Plant - T | n | Existing cap banks | Normal | T004-TRANSMISSION SUBSTATION ADDITI | in service | 2020-01-01 |  | 88060.95 |  |  |  | 0 | 88060.95
C0024162 | C0024162 | #N/A | 83V-301 Melanson Road Upgrade | Distribution Line | Distribution Plant - D | y | 1.6km of 1/0 upgraded to 336ACSR | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-01-01 |  | 1891.83 |  |  |  | 0 | 1891.83
C0029423 | C0029423 | #N/A | 5N-301 Lower Debert BTR | Distribution Line | Distribution Plant - D | y | 550m of #6Cu replaced with #2ACSR | Normal | D055-Identified Deteriorated Plant | in service | 2020-07-01 |  | 2292.5 |  |  |  | 0 | 2292.5
C0025802 | C0025802 | #N/A | 93V-313G Meteghan Shore Rd Ph Ext | Distribution Line | Distribution Plant - D | y | Extend 2 phases, add Vregulator | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-12-31 |  | 4530.81 |  |  |  | 0 | 4530.81
44054-D483 | 44054 | #N/A | 534S-212 Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-01-30 | 2017-06-23 | 83851.21 | FIN Approval - Internal | 2017-06-23 |  | 6 | 94430.0815
45831-D563 | 45831 | #N/A | 10C-212 Voltage Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-08-31 | 2019-02-28 | 137315.79 | FIN Approval - Internal | 2018-11-28 |  | 6 | 154639.8823
46579-D621 | 46579 | #N/A | 48W-204 Wolfe St Voltage Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-09-30 | 2017-07-21 | 165999.25 | FIN Approval - Internal | 2017-07-21 |  | 5 | 183276.5853
51498-D855 | 51498 | #N/A | 553W-211 West Caledonia Rd Convers. | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-12-31 | 2020-03-01 | 599909.25 | FIN Approval - Internal | 2019-07-31 |  | 3 | 636628.4954
39789-D313 | 39789 | #N/A | Highway 10 Three Phase Conversion |  | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2011-02-22 | 2012-10-30 | 49038.25 | zINVALID FIN Approval - External | 2012-09-27 |  | 9 | 58605.2482
36922-D352 | 36922 | #N/A | Dartmouth East New Feeder |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-03-31 | 2014-11-20 | 532588.13 | zINVALID FIN Approval - Internal | 2014-11-20 |  | 9 | 636492.1163
34602-D359 | 34602 | #N/A | 25 kV Feeder Extension Bissett Road |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-05-20 | 2014-08-01 | 1285635.32 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 9 | 1536453.2169
40226-D366 | 40226 | #N/A | Sluice Pt PH 3 Addition 102W-312 |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-09-30 | 2014-11-21 | 385888.39 | FIN Approval - Internal | 2014-11-21 |  | 9 | 461172.3472
40202-D340 | 40202 | #N/A | 39N Maccan Conversion |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-08-01 | 322491.57 | FIN Approval - Internal | 2014-08-08 |  | 9 | 385407.2788
40203-D341 | 40203 | #N/A | Gold River Phase 1 |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-07-23 | 376986.23 | FIN Approval - Internal | 2014-07-23 |  | 9 | 450533.4419
40220-D343 | 40220 | #N/A | 2011 Halifax U/G Cable Replacement |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-07-11 | 510439.85 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 9 | 610022.8715
40338-D355 | 40338 | #N/A | 16W-301 Hebron Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2016-04-30 | 605670.18 | FIN Approval - Internal | 2016-04-18 |  | 9 | 723831.9312
40379-D382 | 40379 | #N/A | Scotch Village Phase 2 |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-11-21 | 295344.88 | FIN Approval - Internal | 2014-11-21 |  | 9 | 352964.4713
41623-D377 | 41623 | #N/A | 22C Cleveland New Feeder |  | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2011-12-20 | 2014-07-23 | 34451.09 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 9 | 41172.2416
41203-D372 | 41203 | #N/A | 93V-311 Saulnierville Reconductor |  | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2011-12-31 | 2012-10-31 | 199876.66 | zINVALID FIN Approval - External | 2012-10-16 |  | 9 | 238871.111
25575-D426 | 25575 | #N/A | Reliability Keltic Drive New Feeder | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-05-31 | 2016-01-31 | 1660864.18 | FIN Approval - Internal | 2016-02-18 |  | 8 | 1945967.0971
41327-D401 | 41327 | #N/A | 103W-311 Gold River Reconductor Ph2 |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-11 | 217178.8 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 254459.5784
41333-D407 | 41333 | #N/A | 16N-301 Stewiacke Reconductor |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-07-23 | 263578.52 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 308824.2456
42067-D398 | 42067 | #N/A | 16V-315 Lewiston Rd Reconductor |  | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2012-09-24 | 2014-07-23 | 116822.63 | zINVALID FIN Approval - Internal | 2014-07-23 |  | 8 | 136876.3304
42128-D414 | 42128 | #N/A | 87H-313 Clam Harbour Phase Addition |  | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-09-24 | 2014-08-01 | 87863.73 | zINVALID FIN Approval - Internal | 2014-08-08 |  | 8 | 102946.3635
42846-D439 | 42846 | #N/A | 63V-313 Feeder Loading Improvement |  | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-09-24 | 2014-07-11 | 295324.56 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 346019.7912
41683-D381 | 41683 | #N/A | 20H-302 Cowie Hill Conversion |  | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2012-09-30 | 2014-07-11 | 54732.48 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 64127.8236
40386-D383 | 40386 | #N/A | Tusket Islands Phase 2 |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-11 | 309017.43 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 362063.1708
41359-D437 | 41359 | #N/A | 79V-402 Feeder Load Reduction | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-12-19 | 2016-01-31 | 402306.41 | FIN Approval - Internal | 2016-02-18 |  | 8 | 471366.0793
41363-D471 | 41363 | #N/A | 88W New Feeder |  | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2012-12-19 | 2014-07-11 | 103938.97 | zINVALID FIN Approval - Internal | 2014-07-11 |  | 8 | 121781.0693
41540-D423 | 41540 | #N/A | 99V Highbury Rd New Feeders | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2013-02-19 | 2017-06-23 | 1244665.72 | FIN Approval - Internal | 2017-06-23 |  | 7 | 1429729.6736
44050-D479 | 44050 | #N/A | 126H-311 Myra RD Phase Extension |  | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-05-22 | 2014-08-01 | 110980.58 | FIN Approval - Internal | 2014-08-08 |  | 7 | 127481.8016
42788-D430 | 42788 | #N/A | 63V-313 Palmer Rd. Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-06-18 | 2016-01-31 | 256953.11 | FIN Approval - Internal | 2016-02-18 |  | 7 | 295158.3547
44108-D486 | 44108 | #N/A | 89W-301 Dayspring Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-06-18 | 2016-01-31 | 253874.62 | FIN Approval - Internal | 2016-02-18 |  | 7 | 291622.1374
44192-D488 | 44192 | #N/A | 103W-311G Indian Point Rd 3 Ph Conv |  | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-06-18 | 2014-07-11 | 119568.8 | FIN Approval - Internal | 2014-07-10 |  | 7 | 137346.9669
44308-D498 | 44308 | #N/A | 16W-301 Hebron Neutral Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2013-08-31 | 2016-04-30 | 41316.41 | FIN Approval - Internal | 2016-04-18 |  | 7 | 47459.568
43551-D526 | 43551 | #N/A | 56N-401 Pictou Rebuild & Conversion | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2013-09-25 | 2016-01-31 | 527623.93 | FIN Approval - Internal | 2016-02-18 |  | 7 | 606074.0463
44407-D508 | 44407 | #N/A | 581N-301 Harmony Overloaded | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-09-25 | 2014-07-23 | 55677.51 | FIN Approval - Internal | 2014-07-23 |  | 7 | 63955.9577
44530-D512 | 44530 | #N/A | 625V Mt. Uniacke Overload Stepdown | Dist - New | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-09-25 | 2016-01-31 | 62046.93 | FIN Approval - Internal | 2016-02-18 |  | 7 | 71272.4192
44051-D480 | 44051 | #N/A | 51V-301 Meadowvale Road Two Phases | Dist - New | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2013-10-28 | 2016-08-30 | 27228.05 | FIN Approval - Internal | 2016-09-12 |  | 7 | 31276.4708
43219-D490 | 43219 | #N/A | 93V-311 Saulnierville Recon Ph 2 | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2014-02-28 | 2016-01-31 | 362525 | FIN Approval - Internal | 2016-02-18 |  | 6 | 408262.031
45878-D576 | 45878 | #N/A | 534N Duchess Avenue Overload | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-07-31 | 2016-01-31 | 91656.77 | FIN Approval - Internal | 2016-02-18 |  | 6 | 103220.4098
45027-D560 | 45027 | #N/A | 535N - Powell Road Phase 1 | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2014-08-31 | 2016-01-31 | 239312.61 | FIN Approval - Internal | 2016-02-18 |  | 6 | 269504.8678
44832-D543 | 44832 | #N/A | 73W-411G East Dalhousie Load Shift | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2014-10-29 | 2016-01-31 | 247352.48 | FIN Approval - Internal | 2016-02-18 |  | 6 | 278559.0673
45953-D579 | 45953 | #N/A | 93V-311- Little Brook - Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-11-24 | 2016-01-31 | 293849.54 | FIN Approval - Internal | 2016-02-18 |  | 6 | 330922.3089
45690-D594 | 45690 | #N/A | 647N-312 West Linden Rd Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-29 | 2017-06-23 | 21753.53 | FIN Approval - Internal | 2017-06-23 |  | 6 | 24498.008
45576-D555 | 45576 | #N/A | 103H-432 - Maplewood Dr. Phase Ext | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2014-12-31 | 2017-06-23 | 52594.52 | FIN Approval - Internal | 2017-06-23 |  | 6 | 59229.9719
45610-D552 | 45610 | #N/A | 65V-303 Gates Mtn Rd Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2016-01-31 | 104582.36 | FIN Approval - Internal | 2016-02-18 |  | 6 | 117776.7235
46085-D590 | 46085 | #N/A | 92H-331G Boutiliers Cove Rd Recondu | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2014-12-31 | 2016-01-31 | 23075.26 | FIN Approval - Internal | 2016-02-18 |  | 6 | 25986.4906
46031-D584 | 46031 | #N/A | 16V-315 Weymouth Add Regulators | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-04-30 | 2017-06-23 | 77740.31 | FIN Approval - Internal | 2017-06-23 |  | 5 | 85831.5839
46932-D620 | 46932 | #N/A | 647N-312 Linden Road Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-05-31 | 2016-08-30 | 174608.87 | FIN Approval - Internal | 2016-09-12 |  | 5 | 192782.3014
46933-D619 | 46933 | #N/A | 6N-302 Rodney Road Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-05-31 | 2017-07-21 | 76336.3 | FIN Approval - Internal | 2017-07-21 |  | 5 | 84281.4434
47071-D634 | 47071 | #N/A | 99V-313 Olympic Ave- Add 2nd Phase | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-05-31 | 2017-06-23 | 25175.45 | FIN Approval - Internal | 2017-06-23 |  | 5 | 27795.7311
45026-D587 | 45026 | #N/A | 639N - Mount Thom Overload | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-06-30 | 2019-02-28 | 160982.78 | FIN Approval - Internal | 2018-11-28 |  | 5 | 177737.997
47312-D647 | 47312 | #N/A | 11S-305 4S-333 Membertou Overload | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-06-30 | 2019-02-28 | 321443.23 | FIN Approval - Internal | 2018-10-01 |  | 5 | 354899.2996
45819-D566 | 45819 | #N/A | Fourchu Overload | Dist - New | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-08-31 | 2016-08-30 | 116609.11 | FIN Approval - Internal | 2016-09-12 |  | 5 | 128745.8798
46196-D597 | 46196 | #N/A | U&U 92H-332 Hubley Load Growth | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-09-30 | 2019-02-28 | 173688.59 | FIN Approval - Internal | 2018-11-28 |  | 5 | 191766.238
46212-D608 | 46212 | #N/A | 500N-301 Caribou Island Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-07-21 | 233351.13 | FIN Approval - Internal | 2017-07-21 |  | 5 | 257638.503
46621-D612 | 46621 | #N/A | 69V-211 - Bridgetown - Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-09-30 | 2016-08-30 | 197352.3 | FIN Approval - Internal | 2016-09-12 |  | 5 | 217892.8859
47121-D648 | 47121 | #N/A | 22N-401-Southampton Rd - Reconducto | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-07-21 | 184837.95 | FIN Approval - Internal | 2017-07-21 |  | 5 | 204076.0323
47251-D651 | 47251 | #N/A | 99V-314GA North River Rd Add 1Ph VR | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-09-30 | 2017-07-21 | 34157.1 | FIN Approval - Internal | 2017-07-21 |  | 5 | 37712.1984
47399-D658 | 47399 | #N/A | 65V-302H - Bloomington Rd Reconduct | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-07-21 | 196215.56 | FIN Approval - Internal | 2017-07-21 |  | 5 | 216637.8331
47616-D668 | 47616 | #N/A | 77V-303 - Victoria Street Reconduct | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-07-21 | 240767.27 | FIN Approval - Internal | 2017-07-21 |  | 5 | 265826.5208
47679-D667 | 47679 | #N/A | 103C-311 Barren Road Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2015-09-30 | 2017-07-21 | 356577.56 | FIN Approval - Internal | 2017-07-21 |  | 5 | 393690.4388
46457-D639 | 46457 | #N/A | 79V-401 Cameron Lake Voltage Conver | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-10-31 | 2017-07-21 | 575570.7 | FIN Approval - Internal | 2017-07-21 |  | 5 | 635476.5608
47275-D653 | 47275 | #N/A | 36V-302 Longspell Rd- Add 2 Phases | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2015-10-31 | 2017-06-23 | 186981.66 | FIN Approval - Internal | 2017-06-23 |  | 5 | 206442.8614
44833-D580 | 44833 | #N/A | 99V-312 - Highbury New Feeder | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-11-30 | 2017-07-21 | 397976.41 | FIN Approval - Internal | 2017-07-21 |  | 5 | 439398.1144
46581-D622 | 46581 | #N/A | 500N-301 Caribou Island Overload | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-11-30 | 2019-04-01 | 119004.36 | FIN Approval - Internal | 2018-10-01 |  | 5 | 131390.4294
46759-D618 | 46759 | #N/A | 127H-411 Fall River Add 2 Phases | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-11-30 | 2017-07-21 | 45134.22 | FIN Approval - Internal | 2017-07-21 |  | 5 | 49831.8259
47225-D654 | 47225 | #N/A | 127H-411-Fall River-Load Growth Ph2 | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2015-11-30 | 2019-02-28 | 127311.66 | FIN Approval - Internal | 2018-11-28 |  | 5 | 140562.3598
47693-D676 | 47693 | #N/A | 63V-313G-Evangeline Trail Reconduct | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2015-11-30 | 2017-07-21 | 413940.82 | FIN Approval - Internal | 2017-07-21 |  | 5 | 457024.113
43177-D570 | 43177 | #N/A | 103W-311 Gold River Reconductor Ph3 | Distribution Line | Distribution Plant - D | y |  | Normal | Special | in service | 2016-01-31 |  | 572007.71 | FIN Approval - Internal | 2020-10-22 |  | 4 | 619159.5411
46251-D655 | 46251 | #N/A | 36V-303 Saxon Double Circuit | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-01-31 | 2019-02-28 | 515499.91 | FIN Approval - Internal | 2018-11-28 |  | 4 | 557993.6811
46304-D626 | 46304 | #N/A | 20W-311 Argyle Sound Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-01-31 | 2019-02-28 | 632921.44 | FIN Approval - Internal | 2018-11-28 |  | 4 | 685094.5214
46458-D610 | 46458 | #N/A | 16N-302 Stewiacke Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-01-31 | 2019-02-28 | 791829.61 | FIN Approval - Internal | 2018-12-18 |  | 4 | 857101.8351
41341-D427 | 41341 | #N/A | 1H-Water Street New Feeder | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-02-29 | 2019-05-01 | 373801.96 | FIN Approval - Internal | 2019-02-11 |  | 4 | 404615.263
47813-D673 | 47813 | #N/A | 535N Powell Road Phase 2 Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-02-29 | 2017-07-21 | 537992.59 | FIN Approval - Internal | 2017-07-21 |  | 4 | 582340.4813
48412-D697 | 48412 | #N/A | Overload Stepdown - Scotch Hill | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-02-29 | 2017-07-21 | 44165.69 | FIN Approval - Internal | 2017-07-21 |  | 4 | 47806.3632
48434-D695 | 48434 | #N/A | 25W-302G Lockes Island Reconductor | Dist - Replace / Refurb | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-02-29 | 2017-07-21 | 31102.76 | FIN Approval - Internal | 2017-07-21 |  | 4 | 33666.6277
48636-D714 | 48636 | #N/A | Overloaded Stepdown 524C Cape Jack | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-02-29 | 2017-06-23 | 25833.15 | FIN Approval - Internal | 2017-06-23 |  | 4 | 27962.6324
46398-D609 | 46398 | #N/A | 20H Spryfield Voltage Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-07-31 | 607212.26 | FIN Approval - Internal | 2019-04-29 |  | 4 | 657266.0782
46593-D664 | 46593 | #N/A | 70V Bridgetown Voltage Conversion | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-03-31 | 2017-06-23 | 617195.65 | FIN Approval - Internal | 2017-06-23 |  | 4 | 668072.4206
46651-D682 | 46651 | #N/A | 23H-Rockingham Voltage Conversion-P | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-03-31 | 2019-05-01 | 703659.01 | FIN Approval - Internal | 2019-03-29 |  | 4 | 761663.1421
47226-D700 | 47226 | #N/A | 22W-311GA - Daniels Head Rd Recondu | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2016-04-30 |  | 301847.05 | FIN Approval - Internal | 2018-10-01 |  | 4 | 326728.9543
48152-D692 | 48152 | #N/A | 20H-Spryfield Voltage Conversion Ph | Distribution Line | Distribution Plant - D | y |  | Normal | Special | in service | 2016-04-30 |  | 468583.68 |  |  |  | 4 | 507210.0449
48672-D717 | 48672 | #N/A | 83V-301 Grand Pre - Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2016-04-30 |  | 96925.46 | FIN Approval - Internal | 2018-10-01 |  | 4 | 104915.235
48637-D720 | 48637 | #N/A | Overloaded Stepdown - 591C Margaree | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-05-30 | 2017-07-21 | 24945.34 | FIN Approval - Internal | 2017-07-21 |  | 4 | 27001.6383
48912-D729 | 48912 | #N/A | 88W-312G Wyman Rd Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2016-05-30 | 2017-06-23 | 50424.38 | FIN Approval - Internal | 2017-06-23 |  | 4 | 54580.9706
46618-D679 | 46618 | #N/A | 555W-301 Waterloo Overloaded Reclos | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-06-30 | 2017-06-23 | 24679 | FIN Approval - Internal | 2017-06-23 |  | 4 | 26713.3433
47471-D675 | 47471 | #N/A | 131H-422G-East Uniacke Rd Load Grow | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-06-30 | 2019-02-28 | 731035.15 | FIN Approval - Internal | 2018-11-28 |  | 4 | 791295.9565
47753-D688 | 47753 | #N/A | 24C-442GB Hwy 16 Reconductor Ph 2 | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-06-30 | 2020-05-01 | 1336079.83 | FIN Approval - Internal | 2020-03-25 |  | 4 | 1446215.7763
47754-D702 | 47754 | #N/A | 63V-313 Ward Rd Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-06-30 | 2018-08-31 | 203211.29 | FIN Approval - Internal | 2018-06-29 |  | 4 | 219962.4356
47784-D698 | 47784 | #N/A | 103H-Lakeside Feeder Reconfiguratio | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-07-31 | 2019-02-28 | 128988.56 | FIN Approval - Internal | 2018-11-28 |  | 4 | 139621.3656
47055-D633 | 47055 | #N/A | 50W-412 Camperdown Overloaded Equip | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2016-09-30 | 2019-04-01 | 146219.44 | FIN Approval - Internal | 2019-01-03 |  | 4 | 158272.6243
47752-D701 | 47752 | #N/A | 4S-333 Bentinck St. Rebuild | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2016-10-31 | 2019-05-01 | 816087.58 | FIN Approval - Internal | 2019-10-31 |  | 4 | 883359.442
47756-D703 | 47756 | #N/A | 36V-303 Reconductor Middle Dyke Rd | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-01-30 | 2019-07-31 | 287678.08 | FIN Approval - Internal | 2019-04-29 |  | 3 | 305286.2799
33622-D821 | 33622 | #N/A | Construct Two New Feeders Elmsdale | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-02-28 | 2017-06-23 | 970648.06 | FIN Approval - Internal | 2017-06-23 |  | 3 | 1030059.4865
47774-D766 | 47774 | #N/A | 546C-311 West Bay Upgrade | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-03-31 | 2020-02-01 | 134002.4 | FIN Approval - Internal | 2019-12-18 |  | 3 | 142204.4189
47776-D761 | 47776 | #N/A | 111S Prime Brook Feeder Exits & Fee | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-09-30 | 1625298.63 | FIN Approval - Internal | 2019-10-31 |  | 3 | 1724779.9085
48610-D728 | 48610 | #N/A | 16N-301 Stewiacke - Load Transfer | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-04-01 | 817135.35 | FIN Approval - Internal | 2018-12-18 |  | 3 | 867150.5705
49311-D758 | 49311 | #N/A | 93V-312 Lower Saulnierville Conduct | Distribution Line | Distribution Plant - D | y |  | Normal | Special | in service | 2017-03-31 |  | 620417.9 |  |  |  | 3 | 658392.4388
50578-D794 | 50578 | #N/A | 83V-303 Sunken Lake Load Transfer | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2017-05-31 | 2019-09-30 | 75896.64 | FIN Approval - Internal | 2019-07-31 |  | 3 | 80542.1215
50733-D810 | 50733 | #N/A | 70V-311 Arlington Road Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-08-30 | 2020-11-01 | 187112.32 | FIN Approval - Internal | 2020-06-17 |  | 3 | 198565.0909
47734-D775 | 47734 | #N/A | 1C-411 Highway 4 Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2017-09-27 | 2020-11-01 | 586353.96 | FIN Approval - Internal | 2020-06-17 |  | 3 | 622243.5132
50719-D816 | 50719 | #N/A | 7N-301G-Ferry Rd - Phase Extension | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2017-10-31 | 2019-04-01 | 176000.1 | FIN Approval - Internal | 2018-12-18 |  | 3 | 186772.7141
51518-D869 | 51518 | #N/A | 64V-301G Tremont Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2017-12-25 | 2020-03-01 | 282460.1 | FIN Approval - Internal | 2019-07-31 |  | 3 | 299748.9178
49891-D790 | 49891 | #N/A | 509V Recloser and Voltage Regulator | Distribution Line | Distribution Plant - D | y |  | Normal | Special | in service | 2017-12-31 |  | 138465.05 |  |  |  | 3 | 146940.2188
51572 | 51572 | #N/A | Mount Hope Ave Mini Sub | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2017-12-31 | 2019-04-01 | 96423.67 | FIN Approval - Internal | 2018-12-18 |  | 3 | 102325.57
51017-D833 | 51017 | #N/A | 99V-312 North Kentville Phase Exten | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | posted to CPR | 2018-01-31 | 2020-02-01 | 217761.14 | FIN Approval - Internal | 2019-12-18 |  | 2 | 226558.6901
47786-D777 | 47786 | #N/A | 129H Kearney Lake Load Transfer | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2018-02-28 | 2020-05-01 | 315885.74 | FIN Approval - Internal | 2020-03-02 |  | 2 | 328647.5239
48972-D730 | 48972 | #N/A | 12V-302H Granville Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-02-28 | 2020-11-01 | 280450.55 | FIN Approval - Internal | 2020-06-17 |  | 2 | 291780.7522
C0005761 | C0005761 | #N/A | D-67C-411H Reconductor Ceilidh Trai | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-07-31 |  | 387984.12 | FIN Approval - Internal | 2020-10-22 |  | 2 | 403658.6784
51451-D854 | 51451 | #N/A | 78W-301 Northwest Line Extension | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | posted to CPR | 2018-08-31 | 2020-11-01 | 114344.36 | FIN Approval - Internal | 2020-06-17 |  | 2 | 118963.8721
49041-D738 | 49041 | #N/A | 16W-301 Sandford Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-09-01 |  | 544424.15 | FIN Approval - Internal | 2020-10-01 |  | 2 | 566418.8857
C0005878 | C0005878 | #N/A | D-129H-412 Bedford Highway- Recondu | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-09-30 | 2020-05-01 | 65191.16 | FIN Approval - Internal | 2020-03-02 |  | 2 | 67824.8829
C0005078 | C0005078 | #N/A | D-663V-221 West Main St Reconductor | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | posted to CPR | 2018-10-01 | 2020-11-01 | 240460.72 | FIN Approval - Internal | 2020-08-12 |  | 2 | 250175.3331
C0005740 | C0005740 | #N/A | D-21W-312 Lower Woods Harbour Recon | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2018-10-01 |  | 208456.34 | FIN Approval - Internal | 2020-10-22 |  | 2 | 216877.9761
C0007779 | C0007779 | #N/A | D-541C 542C Overloaded Stepdown Why | Distribution Line | Distribution Plant - D | y |  | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2018-10-01 |  | 65851.74 |  |  |  | 2 | 68512.1503
52206 | 52206 | #N/A | D-20V-311 Bishop Ville Rd Reconduct | Distribution Line | Distribution Plant - D | y |  | Normal | Special | posted to CPR | 2018-10-31 | 2020-11-01 | 167852.83 | FIN Approval - Internal | 2020-06-11 |  | 2 | 174634.0843
C0016058 | C0016058 | #N/A | D-36V-303 North Aldershot Rd Recond | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-04-18 |  | 132504.42 |  |  |  | 1 | 135154.5084
C0015358 | C0015358 | #N/A | D - 54C-213 Conversion and Stepdown | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-04-30 |  | 224350.88 |  |  |  | 1 | 228837.8976
C0019280 | C0019280 | #N/A | 22W-312 Hwy 330 Centreville Rcndctr | Distribution Line | Distribution Plant - D | y |  | Normal | D055-Identified Deteriorated Plant | in service | 2019-06-01 |  | 140942.64 | FIN Approval - Internal | 2020-08-12 |  | 1 | 143761.4928
C0023982 | C0023982 | #N/A | 58C-SW Margaree Feeder Exit | Distribution Line | Distribution Plant - D | y |  | Normal | D051 - System Perf. Improvement | in service | 2019-12-01 |  | 110293.37 |  |  |  | 1 | 112499.2374
C0015539 | C0015539 | #N/A | D-139H-412- Commissioning New Feede | Distribution Line | Distribution Plant - D | y | New Feeder at 139H | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-02-01 |  | 157104.22 |  |  |  | 0 | 157104.22
47787-D863 | 47787 | #N/A | 2H Armdale New Feeders | Distribution Line | Distribution Plant - D | y | 4 New Feeders at 2H | Normal | Special | in service | 2020-02-29 |  | 1723438.6 |  |  |  | 0 | 1723438.6
C0011320 | C0011320 | #N/A | D-22W-311GA-Hawk Point Rd Recon | Distribution Line | Distribution Plant - D | y | Reconductor 2.3km lijne | Normal | Special | in service | 2020-03-30 |  | 542223 |  |  |  | 0 | 542223
C0011319 | C0011319 | #N/A | D-21W-311-Lower Harbour Rebuild | Distribution Line | Distribution Plant - D | y | replace 1.9km 1/0 with 336, replace 42 poles | Normal | Special | in service | 2020-03-31 |  | 798173.87 |  |  |  | 0 | 798173.87
C0026963 | C0026963 | #N/A | 85S-401 - Ingonish Reconductor | Distribution Line | Distribution Plant - D | y | Replace 1km conductor with 336ACSR | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-04-01 |  | 154808.55 |  |  |  | 0 | 154808.55
52200 | 52200 | #N/A | D-65V-301 Brickton Reconductor | Distribution Line | Distribution Plant - D | y | Replace 5.1km #2 with #2/0ACSR | Normal | Special | in service | 2020-04-30 |  | 485463.78 |  |  |  | 0 | 485463.78
52184 | 52184 | #N/A | 37N-412-Glooscap Trail Rebuild PH2 | Distribution Line | Distribution Plant - D | y | 5.5km primary upgraded to 2/0ACSR | Normal | Special | in service | 2020-05-30 |  | 422542.64 |  |  |  | 0 | 422542.64
C0015681 | C0015681 | #N/A | D-87H-311-East Chezzetcook Rd- 3-Ph | Distribution Line | Distribution Plant - D | y | Load Balancing upgrades | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-05-31 |  | 172.17 |  |  |  | 0 | 172.17
C0028343 | C0028343 | #N/A | 65V-301 Den Haan Greenhouse Recon | Distribution Line | Distribution Plant - D | y | Load growth related | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-05-31 |  | 144655.12 |  |  |  | 0 | 144655.12
C0028742 | C0028742 | #N/A | 82V-402 Robert St Line Extension | Distribution Line | Distribution Plant - D | y | Load Balancing upgrades | Normal | D004 NEW CUSTOMER REPLACEMENTS.ROUT | in service | 2020-06-02 |  | 50176.25 |  |  |  | 0 | 50176.25
52201 | 52201 | #N/A | D-55V-314GA-Welsford Reconductor | Distribution Line | Distribution Plant - D | y | 3.2km upgrade from #4 to 2/0ACSR | Normal | Special | in service | 2020-07-31 |  | 417632.41 |  |  |  | 0 | 417632.41
49056-D746 | 49056 | #N/A | 65V-302HAA Old Liverpool Rd Rebuild | Distribution Line | Distribution Plant - D | y | Rebuild 2km with upgrade to 2/0ACSR | Normal | Special | in service | 2020-09-30 |  | 254838.36 |  |  |  | 0 | 254838.36
C0032522 | C0032522 | #N/A | 137H/131 Recon and Protection Upgrd | Distribution Line | Distribution Plant - D | y | Reconfiguration required due to load growth | Normal | D051 - System Perf. Improvement | in service | 2020-09-30 |  | 59092.5 |  |  |  | 0 | 59092.5
C0031482 | C0031482 | #N/A | 85S-401 Ingonish Centre BTR | Distribution Line | Distribution Plant - D | y | relocating line to roadside with conductor upgrade | Normal | D055-Identified Deteriorated Plant | in service | 2020-10-31 |  | 26202.61 |  |  |  | 0 | 26202.61
C0020825 | C0020825 | #N/A | 64N-Lourdes Street conversion Phase | Distribution Line | Distribution Plant - D | y |  | Normal | Special | in service | 2020-12-31 |  | 322741.82 |  |  |  | 0 | 322741.82
40425-T647 | 40425 | #N/A | Kempt Road Transformer |  | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2011-12-20 | 2014-11-21 | 1050733.39 | FIN Approval - Internal | 2014-11-21 |  | 9 | 1255723.666
33525-T674 | 33525 | #N/A | Canaan Rd 43V to Tremont 51V Line | Capital Projects Group | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2011-12-31 | 2017-06-23 | 7197372.76 | FIN Approval - Internal | 2017-06-23 |  | 9 | 8601526.6991
25391-T683 | 25391 | #N/A | 25 kV Bus Keltic Dr |  | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2012-09-24 | 2014-11-21 | 775762.01 | zINVALID FIN Approval - Internal | 2014-11-21 |  | 8 | 908928.8364
41552-T705 | 41552 | #N/A | 131H Lucasville Transformer Additio | Trans - New | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2012-10-04 | 2016-08-31 | 1848858.71 | FIN Approval - Internal | 2016-09-12 |  | 8 | 2166232.6517
40321-T687 | 40321 | #N/A | Canaan Rd to Highbury Trans Line | Trans - New | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2012-12-07 | 2017-01-17 | 2044742.03 | FIN Approval - Internal | 2017-01-17 |  | 8 | 2395741.1812
40322-T678 | 40322 | #N/A | Highbury Road Substation | Transmission Line | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2012-12-21 | 2016-09-12 | 3066205.32 | FIN Approval - Internal | 2016-09-12 |  | 8 | 3592548.2273
44092-T765 | 44092 | #N/A | 91W Transformer Replacement | Substation Operations | Transmission Plant - T | y |  | Normal | T003-TRANSMISSION SUBSTATION REPLAC | posted to CPR | 2013-05-22 | 2014-07-23 | 327396.23 | FIN Approval - Internal | 2014-07-23 |  | 7 | 376075.357
43726-T778 | 43726 | #N/A | Replace 3N-T51 Transformer | Substation Operations | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2013-06-30 | 2017-06-23 | 825135.97 | FIN Approval - External | 2017-06-23 |  | 7 | 947821.8626
45182-T784 | 45182 | #N/A | U&U - 40H Install 25kV Transformer | Substation Operations | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2013-10-28 | 2017-01-16 | 119931.01 | FIN Approval - Internal | 2017-01-16 |  | 7 | 137763.0323
40317-T703 | 40317 | #N/A | 1H Transformer & Breaker Addition | Capital Projects Group | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2014-10-04 | 2017-06-29 | 4330201 | FIN Approval - Internal | 2017-07-24 |  | 6 | 4876509.6341
45882-T819 | 45882 | #N/A | 103H-T63 Transformer Replacement | Substation Operations | Transmission Plant - T | y |  | Normal | Special | in service | 2015-11-30 |  | 1402349.23 | FIN Approval - External | 2019-09-20 |  | 5 | 1548306.8642
46362-T843 | 46362 | #N/A | L5560 Reconductor | Transmission Line | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2016-02-29 | 2019-08-31 | 799126.5 | FIN Approval - Internal | 2019-08-23 |  | 4 | 865000.2235
46360-T850 | 46360 | #N/A | L5545B Reconductor | Transmission Line | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2017-03-31 | 2019-05-01 | 808274 | FIN Approval - Internal | 2019-10-31 |  | 3 | 857746.835
46587-T856 | 46587 | #N/A | Metro Voltage Support Add Capacitor | Capital Projects Group - Transmission | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2017-06-12 | 2019-07-31 | 3234346.57 | FIN Approval - Internal | 2019-06-28 |  | 3 | 3432314.4549
49253-T910 | 49253 | #N/A | U&U 20V-T1 Transformer Replacement | Substation Operations | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2017-10-31 | 2019-08-31 | 953531.29 | FIN Approval - External | 2019-07-30 |  | 3 | 1011895.0332
45306-T822 | 45306 | #N/A | Prime Brook Substation Addition | Substation Operations | Transmission Plant - T | y |  | Normal | Special | posted to CPR | 2017-12-22 | 2019-02-28 | 3691720.16 | FIN Approval - Internal | 2018-10-01 |  | 3 | 3917682.9676
48022-T888 | 48022 | #N/A | Spider Lake Substation Addition | MDRR Transmission | Transmission Plant - T | y |  | Normal | Special | in service | 2018-03-31 |  | 9066397.53 |  |  |  | 2 | 9432679.9902
49879-T928 | 49879 | #N/A | 77V-T52 Replacement | Substation Operations | Transmission Plant - T | y |  | Normal | Special | in service | 2019-04-30 |  | 865629.5 |  |  |  | 1 | 882942.09
46811-T872 | 46811 | #N/A | 2H Armdale Transformer Addition | Substation Operations | Transmission Plant - T | y |  | Normal | Special | in service | 2019-06-30 |  | 2817126.85 |  |  |  | 1 | 2873469.387
C0024602 | C0024602 | #N/A | L6537 River Inhabitants Crossing | Transmission Line | Transmission Plant - T | y |  | Normal | Special | in service | 2020-02-29 |  | 437755.73 |  |  |  | 0 | 437755.73
C0021122 | C0021122 | #N/A | 2020-21 Transmission Switch and Br | Substation Operations | Transmission Plant - T | y |  | Normal | Special | in service | 2020-07-31 |  | 666509.51 |  |  |  | 0 | 666509.51
52328 | 52328 | #N/A | 56N-T1 Transformer Upgrades | Substation Operations | Transmission Plant - T | y |  | Normal | Special | in service | 2020-11-30 |  | 1147436.95 |  |  |  | 0 | 1147436.95
[13 empty] | 973807469.01 |  |  |  |  | 1052600868.7301
found manually
[5 empty] | 2109 $ |  |  | 2010 - 2019 | Total Cost (2019 $) | Average Yearly Cost (2020 $) | Carrying Charge | Carrying Costs
| 41519 | Harbour East 138 kV Transmission Line | Cancelled | 636580.21 | 675544.0115 |  |  | Transmission | 53008155.1947 | 5300815.5195 | 9.6% | 508878.2899
| 48025 | L7018 Upgrade to 345kV & Capacitor Bank Addition | Cancelled | 0 | - |  |  | Distribution | 46151629.9239 | 4615162.9924 | 9.6% | 443055.6473
| 48154 | L5527 Reconductor | Cancelled | 0 | - |  |  | Period of Years | 10
| 50342 | Western Transmission System Voltage Support | [5 empty] | Avoided T&D Costs | Growth (MW, PF=.97) | Transmission $/kW-yr | Distribution $/kW-yr | Total $/kW-yr
[5 empty] | Transmission Plant - T |  |  | Constrained System | 7.1093 | 71.5797 | 62.321 | 133.9006 | Projected Growth = Growth rate x Constrained System MVA x PF (Snapshot Summary Tab)
[5 empty] | Distribution Plant - D |  |  | System Wide | 21.936 | 23.1983 | 20.1976 | 43.396 | Projected Growth = 10 Year Linear Approximation of system wide growth in MW / 10
10 Years Historic Data to Determine System Co-incident Peak Load Growth with 2010 & 2011 Impacts of Bowater & NewPage PM1 Contribution to Co-incident Peak Removed
[8 empty] | Figure 2: Coincident Peak Demand with Future DSM Program Effects (2020 Outlook Report) | [6 empty] | System Peak
[8 empty] | Year | Interruptible Contribution to Peak (MW) | Firm Contribution to Peak (MW) | System Peak (MW) |  |  |  | y=21.936x+1944.4 | incremental Growth/yr | Equivalent Growth/yr | 1.075%
[8 empty] | 2010 | (295) 141 | 1820 | 1961 |  | 2010 | 0 | 1944.4 |  | 1944.4
[8 empty] | 2011 | 265 (141) | 1903 | 2044 |  | 2011 | 1 | 1966.336 | 21.936 | 1965.3023
[8 empty] | 2012 | 141 | 1740 | 1881 |  | 2012 | 2 | 1988.272 | 21.936 | 1986.4293
[8 empty] | 2013 | 136 | 1897 | 2033 |  | 2013 | 3 | 2010.208 | 21.936 | 2007.7834
[8 empty] | 2014 | 83 | 2036 | 2119 |  | 2014 | 4 | 2032.144 | 21.936 | 2029.3671
[8 empty] | 2015 | 141 | 1874 | 2015 |  | 2015 | 5 | 2054.08 | 21.936 | 2051.1828
[8 empty] | 2016 | 98 | 2013 | 2111 |  | 2016 | 6 | 2076.016 | 21.936 | 2073.233
[8 empty] | 2017 | 67 | 1951 | 2018 |  | 2017 | 7 | 2097.952 | 21.936 | 2095.5203
[8 empty] | 2018 | 80 | 1993 | 2073 |  | 2018 | 8 | 2119.888 | 21.936 | 2118.0471
[8 empty] | 2019 | 111 | 1949 | 2060 |  | 2019 | 9 | 2141.824 | 21.936 | 2140.8161
[8 empty] | 2020 | 147 | 2098 | 2245 |  | 2020 | 10 | 2163.76 | 21.936 | 2163.8299
[8 empty] | 2021 | 152 | 2085 | 2237
[8 empty] | 2022 | 159 | 2053 | 2212
[8 empty] | 2023 | 161 | 2059 | 2220 |  | Total Growth for Transmission System including losses
[8 empty] | 2024 | 166 | 2064 | 2230
[8 empty] | 2025 | 166 | 2070 | 2236 |  |  |  | Total | 219.36
[8 empty] | 2026 | 165 | 2074 | 2239
[8 empty] | 2027 | 165 | 2075 | 2240
[8 empty] | 2028 | 165 | 2075 | 2240
[8 empty] | 2029 | 165 | 2076 | 2241
[8 empty] | 2030 | 164 | 2076 | 2240
[8 empty] | - New Page mIll with two paper machines and three TMP lines shut down Sep 2011; | [6 empty] | System Peak
[8 empty] | - PHP (New Page mill) started up again with PM1 retired in Sep, 2012. PM1 load approx 30MW | [6 empty] | y=16.3x+1989.5 | incremental Growth/yr | Equivalent Growth/yr | 0.79%
[8 empty] | - Bowater Mersey shut down on Jun 15, 2012. Load approx. 100MW |  |  |  |  | 2010 | 0 | 1989.5 |  | 1989.5
[13 empty] | 2011 | 1 | 2005.8 | 16.3 | 2005.217
[13 empty] | 2012 | 2 | 2022.1 | 16.3 | 2021.0583
[13 empty] | 2013 | 3 | 2038.4 | 16.3 | 2037.0246
[13 empty] | 2014 | 4 | 2054.7 | 16.3 | 2053.1171
[13 empty] | 2015 | 5 | 2071 | 16.3 | 2069.3367
[13 empty] | 2016 | 6 | 2087.3 | 16.3 | 2085.6845
[13 empty] | 2017 | 7 | 2103.6 | 16.3 | 2102.1614
[13 empty] | 2018 | 8 | 2119.9 | 16.3 | 2118.7685
[13 empty] | 2019 | 9 | 2136.2 | 16.3 | 2135.5068
[13 empty] | 2020 | 10 | 2152.5 | 16.3 | 2152.3773
Total Growth for Transmission System including losses
[15 empty] | Total | 163
System Peak
[15 empty] | y=22.627x+1822.3 | incremental Growth/yr | Equivalent Growth/yr | 1.178%
[13 empty] | 2010 | 0 | 1822.3 |  | 1822.3
[13 empty] | 2011 | 1 | 1844.927 | 22.627 | 1843.7667
[13 empty] | 2012 | 2 | 1867.554 | 22.627 | 1865.4863
[13 empty] | 2013 | 3 | 1890.181 | 22.627 | 1887.4617
[13 empty] | 2014 | 4 | 1912.808 | 22.627 | 1909.696
[13 empty] | 2015 | 5 | 1935.435 | 22.627 | 1932.1922
[13 empty] | 2016 | 6 | 1958.062 | 22.627 | 1954.9534
[13 empty] | 2017 | 7 | 1980.689 | 22.627 | 1977.9828
[13 empty] | 2018 | 8 | 2003.316 | 22.627 | 2001.2834
[13 empty] | 2019 | 9 | 2025.943 | 22.627 | 2024.8585
[13 empty] | 2020 | 10 | 2048.57 | 22.627 | 2048.7114
Total Growth for Transmission System including losses
[15 empty] | Total | 226.27
Formulas:
FIN Date = IFERROR(VLOOKUP([Fp Number],[1]Approval!A:J,10,FALSE),"")
2011-2020 Co-incident Peak Load Growth Inc. PHP
Set PHP 2012 load at 265MW

## Matter & CI#
Matter |  |  |  |  | Header
M05095 | G |  | 10900 | M05095 | CI# 10900 - P-128.12 - NSPI WO - HYD DEB #10 – Generator Rewind – $985,901
M06220 | G |  | 12079 | M06220 | CI# 12079 - P-128.11 - NSPI WO - Q1 2014 - HYD - SHH - RUF 1 and 2 Runner Replacement - $1,304,966
M05096 | G |  | 14366 | M05096 | CI# 14366 - P-128.12 - NSPI WO - SHH DIB – Pipeline Replacement – $3,820,694
M05224 | G |  | 14719 | M05224 | CI# 14719 - P-128.12 - NSPI WO - POT - Condenser Tube Replacement - $2,088,744
M09579 | G |  | 16374 | M09579 | P-128.20 Nova Scotia Power Inc. (NSPI) - CI 16374 - HYD - Gaspereau Dam Safety Remedial Works – Authorization to Overspend - $18,348,561
M08053 | G |  | 17581 | M08053 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 17581 ‐ HYD Weymouth Electrical Replacement – $2,366,025
M05588 | G |  | 17830 | M05588 | CI# 17830 - P-128.13 - NSPI WO - HYD - STM Big Indian Dam Safety - Outside Quarter March 13, 2013 - $3,270,949
M05389 | G |  | 18448 | M05389 | CI# 18448 - P-128.12 - NSPI WO - TUC Cooling Water System Biofouling Control - $3,525,7213
M06221 | G |  | 18448 | M06221 | CI# 18448 - P-128.12 - NSPI WO - Q1 2014 - TUC Cooling Water System Biofouling Control - $4,416,543
M05097 | G |  | 19753 | M05097 | CI# 19753 - P-128.12 - NSPI WO - HYD ANN-Unit Overhaul – $2,695,919
M08091 | G |  | 20511 | M08091 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 20511 - CT Victoria Junction Replace Halon Fire Protection System - $619,750
M07459 | G |  | 20571 | M07459 | P-516 - CI# 20571 - NSPI WO - ATO - HYD Weymouth Tailrace Deck Refurbishment - $1,012,394; ATO amount $640,925; $68,559 spent as at March 31, 2016
M06139 | G |  | 20758 | M06139 | CI# 20758 - P-514 - NSPI WO - HYD-U &U Nictaux Intake & Pipeline Replacement - Outside Quarter March 4, 2014 - $4,472,431
M08955 | G |  | 20758 | M08955 | P-518 - Nova Scotia Power Inc. (NSPI) - (FIN) CI 20758 – HYD Nictaux Intake & Pipeline Replacement – $3,522,588
M07553 | G |  | 23125 | M07553 | P-516 - CI #23125 - ATO NSPI Work Order - HYD-Sissiboo - Powerhouse Electrical Refurbishment- $1,208,257; ATO amount $362,501; $1,205,846 spent as at May 31, 2016
M07939 | G |  | 23125 | M07939 | P-517 - Nova Scotia Power Inc. (NSPI) - ATO/FIN - CI 23125 – HYD Sissiboo Powerhouse Electrical Refurbishment – $1,203,547
M05394 | O |  | 25566 | M05394 | CI# 25566 - P-128.12 - NSPI WO - Replace DNR Microwave Circuits - $2,205,252
M05396 | D |  | 28295 | M05396 | CI# 28295 - P-128.12 - NSPI WO - Construct 137H Hammonds Plains Rd. 138/25 kV Substation - $4,003,879
M05516 | D |  | 28474 | M05516 | CI# 28474 - P-128.12 - NSPI WO -St. Croix Install New Transformer & Bus - $4,070,458
M04940 | G |  | 28487 | M04940 | CI# 28487 - P-128.12 - NSPI WO - LIN Supplemental Water Supply - $3,367,744
M05403 | G |  | 28552 | M05403 | CI# 28552 - P-128.12 - NSPI WO - TRE5 Replace Trenton 5 Generator - $15,834,753
M05226 | G |  | 28570 | M05226 | CI# 28570 - P-128.12 - NSPI WO - HYD - Hollow Bridge Generator Rewind - $1,492,476
M05393 | D |  | 28702 | M05393 | CI# 28702 - P-128.12 - NSPI WO - Replace Bridgewater Transformer 89W-T1 - $1,773,084
M05228 | G |  | 28726 | M05228 | CI# 28726 - P-128.12 - NSPI WO - HYD - Carleton Lake Dam Refurbishment - $6,321,508
M05227 | G |  | 28727 | M05227 | CI# 28727 - P-128.12 - NSPI WO - HYD - Great Barren Dam Safety - $2,301,559
M05405 | G |  | 28752 | M05405 | CI# 28752 - P-128.12 - NSPI WO - LM6000 Overhaul TUC#5 Engine - $943,711
M05401 | G |  | 28865 | M05401 | CI# 28865 - P-128.12 - NSPI WO - POT Unit#2 Low NOx Combustion Firing System - $3,561,731
M05391 | D |  | 29008 | M05391 | CI# 29008 - P-128.12 - NSPI WO - Construct 139H Dartmouth Crossing Substation - $4,681,153
M07239 | D |  | 29010 | M07239 | P-515 - CI #29010 - NSPI WO - Final Cost Capital Item - Install 138-25kV Transformer at 22C
M07734 | D |  | 29010 | M07734 | P-516 - CI 29010 (FIN) - Install 138‐25kV Transformer at 22C – $2,338,356 Increased spend amount $599,812
M07734 | D |  | 29010 | M07734 | P-516 - CI 29010 (FIN) - Install 138‐25kV Transformer at 22C – $2,338,356 Increased spend amount $599,812
M05098 | T |  | 29012 | M05098 | CI# 29012 - P-128.12 - NSPI WO - Upgrade L6537 – $2,234,560
M05395 | D |  | 29013 | M05395 | CI# 29013 - P-128.12 - NSPI WO - 82V Elmsdale Transformer Addition - $2,920,567
M08162 | G |  | 29807 | M08162 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 29807 - Tusket Main Dam Refurbishment Application - 18,157,609
M05223 | G |  | 29822 | M05223 | CI# 29822 - P-128.12 - NSPI WO - Pt. Tupper - Relocate Port Malcolm Rd. - $1,632,187
M06690 | G |  | 30162 | M06690 | CI# 30162 - P-128.14 - NSPI WO - POT Bunker C Tank Refurbishment - $2,391,564. ACE amount $2,239,835. $1,298,042 spent to date
M07762 | G |  | 30163 | M07762 | P-128.16 - CI 30163 - POT - Control & Permit Room Upgrade - $387,997 (Partially Confidential)
M05099 | G |  | 31203 | M05099 | CI# 31203 - P-128.12 - NSPI WO - HYD – Toms Lake Safety Remedial Works – $2,008,811
M05404 | G |  | 31244 | M05404 | CI# 31244 - P-128.12 - NSPI WO - Paradise Wood Stave Pipeline Replacement - $9,386,935
M07585 | G |  | 31246 | M07585 | P-516 - (FIN) - CI #31246 - HYD - Methals Intake Replacement - $4,701,112; Decreased spend amount ($1,920,980)
M05100 | G |  | 32442 | M05100 | CI# 32442 - P-128.12 - NSPI WO - HYD – Ridge Spillway Refurbishment – $1,569,003
M07156 | G |  | 33142 | M07156 | CI# 33142 - P-515 - NSPI WO - CT- Burnside Unit # 4 Restoration - Subsequent Approval Item -
M08293 | G |  | 33142 | M08293 | P-517 - Nova Scotia Power Inc. (NSPI) (ATO) - CI 33142 – Burnside 4 Restoration – $9,552,963 (Filed outside Quarter Package Sept. 2017)
M07575 | G |  | 33624 | M07575 | P-516 - (FIN) - CI #33624 -Spare Generator Transformer - $3,520,466; Decreased spend amount ($831,194)
M05225 | G |  | 33942 | M05225 | CI# 33942 - P-128.12 - NSPI WO - Coon Pond Pipeline Replacement - $1,600,480
M05950 | G |  | 34182 | M05950 | CI# 34182 - P-128.09 - NSPI - WO - LIN Unit #1 Mercury Abatement - Outside Quarter October 30, 2013 - $2,038,874
M05951 | G |  | 34202 | M05951 | CI# 34202 - P-128.09 - NSPI - WO - LIN Unit #2 Mercury Abatement - Outside Quarter October 30, 2013 - $1,962,692
M05952 | G |  | 34222 | M05952 | CI# 34222 - P-128.09 - NSPI - WO - LIN Unit #4 Mercury Abatement - Outside Quarter October 30, 2013 - $1,968,862
M05953 | G |  | 34223 | M05953 | CI# 34223 - P-128.09 - NSPI - WO - POT Mercury Abatement - Outside Quarter October 30, 2013 - $2,831,834
M05954 | G |  | 34224 | M05954 | CI# 34224 - P-128.09 - NSPI - WO - TRE Unit #5 Mercury Abatement - Outside Quarter October 30, 2013 - $1,864,202
M05955 | G |  | 34242 | M05955 | CI# 34242 - P-128.09 - NSPI - WO - TRE Unit #6 Mercury Abatement - Outside Quarter October 30, 2013 - $2,122,584
M05515 | O |  | 34583 | M05515 | CI# 34583 - P-128.12 - NSPI WO - Transportation Vehicle Replacements - $1,406,537
M05652 | O |  | 34843 | M05652 | CI# 34843 - P-128.13 - NSPI WO (Q1 2013) - Oracle NLA License
M07586 | G |  | 36902 | M07586 | P-516 - (FIN) - CI #36902 - LIN1 - ESP Gas Flow Modification - $536,885; Decreased spend amount ($957,393)
M05101 | G |  | 37609 | M05101 | CI# 37609 - P-128.12 - NSPI WO - LIN – Unit $1 Rotor Rewind – $3,461,093
M05397 | D |  | 38022 | M05397 | CI# 38022 - P-128.12 - NSPI WO - 2010 Recloser Additions - $1,654,432
M07154 | G |  | 38108 | M07154 | CI# 38108 -P-128.15 - NSPI WO - POT-AVR Replacement -Nova Scotia Power Inc.
M05946 | G |  | 38163 | M05946 | CI# 38163 - P-513 - NSPI - WO - TRE6 U&U Pulverizer Refurbishment - Outside Quarter October 30, 2013 - $714,877
M05400 | G |  | 38362 | M05400 | CI# 38362 - P-128.12 - NSPI WO - TUC#1 Generator Rotor Restore- $3,629,169
M05102 | G |  | 38442 | M05102 | CI# 38442 - P-128.12 - NSPI WO - LIN – U&U – Unit #2 ESP Flow Modifications – $1,691,228
M05221 | D |  | 38732 | M05221 | CI# 38732 - P-128.12 - NSPI WO - 1H Water Street Replace - $1,632,493
M04938 | G |  | 38826 | M04938 | CI# 38826 - P-128.12 - NSPI WO - POT Distribution Control, SYstem (DCS) Upgrade - $1,349,773
M05222 | G |  | 38826 | M05222 | CI# 38826 - P-128.12 - NSPI WO - POT DCS Upgrade - $1,349,493
M04939 | G |  | 38834 | M04939 | CI# 38834 - P-128.12 - NSPI WO - TRE5 Turbine Upgrades LP/IP/HP - $5,929,964
M05069 | G |  | 38834 | M05069 | CI# 38834 - P-128.12 - NSPI WO - TRE5 - Turbine Upgrades LP/IP/HP -
M07157 | D |  | 38888 | M07157 | CI# 38888 -P-515 - NSPI WO -50N-412 Targeted Feeder Replacements - ATO/FIN
M08358 | G |  | 38931 | M08358 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 38931 – HYD Harmony Stabilization - $931,942 - 3rd Quarter 2017
M05402 | G |  | 38942 | M05402 | CI# 38942 - P-128.12 - NSPI WO - TUC #3 Generator Rotor Rewind - $1,445,911
M05103 | G |  | 38943 | M05103 | CI# 38943 - P-128.12 - NSPI WO - LIN1 – Boiler Refurbishment – $1,651,741
M05392 | D |  | 39270 | M05392 | CI# 39270 - P-128.12 - NSPI WO - 2011 Dist. Cutout Replacements - $3,217,257
M05399 | G |  | 39529 | M05399 | CI# 39529 - P-128.12 - NSPI WO - POT Steam Turbine / Generator Major 2011 - $5,177,978
M05062 | G |  | 39783 | M05062 | CI# 39783 - P-128.12 - NSPI WO - TUC - U&U Security System Upgrade
M05585 | G |  | 39803 | M05585 | CI# 39803 - P-128.13 - NSPI WO - POT Unit #2 Generator Major Refurbishment - Outside Quarter March 13, 2013 - $2,999,568
M07587 | G |  | 39932 | M07587 | P-516 - (FIN) - CI #39932 -TRE - Ash Site Phase 2 Development- $5,319,429; Decreased spend amount ($463,908)
M05104 | T&D |  | 40224 | M05104 | CI# 40224 - P-128.12 - NSPI WO - 78w -301 Second Peninsula – $519,245
M05390 | D |  | 40224 | M05390 | CI# 40224 - P-128.12 - NSPI WO - 78W-301 Second Peninsula (Re-File) - $422,878
M07574 | T |  | 40260 | M07574 | P-516 - (FIN) - CI #40260 - L-7012 Beaver Narrows Crossing Replacement - $1,099,112; Decreased spend amount ($800,112)
M07505 | G |  | 40271 | M07505 | CI# 40271 - P-516 - Nova Scotia Power Inc. (NSPI) - FIN - LIN2 Boiler Refurbishment - $505,247; Decreased spend amount ($588,457);
M05651 | O |  | 40278 | M05651 | CI# 40278 - P-128.13 - NSPI WO - OMS Replacement 2011 (Q1 2013) - $4,102,903
M05586 | T |  | 40280 | M05586 | CI# 40280 - P-128.13 - NSPI WO - 2011 Transmission Switch & Breaker Upgrade - Outside Quarter March 13, 2013 - $3,275,925
M05398 | T |  | 40281 | M05398 | CI# 40281 - P-128.12 - NSPI WO - 2011 Transmission Line Insulator Replacement - $3,986,553
M06693 | G |  | 40283 | M06693 | CI# 40283 - P-128.15 - NSPI WO - HYD - Wrights Lake Dam Refurbishment - $1,600,449. ACE amount $2,242,751. $275,406 spent to date
M05587 | T |  | 40287 | M05587 | CI# 40287 - P-128.13 - NSPI WO - Substation Recloser Replacement - Outside Quarter March 13, 2013 - $4,234,195
M07588 | G |  | 40308 | M07588 | P-516 - (FIN) - CI #40308 - HYD - Weymouth Falls Pipeline Replacement - $5,949,340; Decreased spend amount ($803,420)
M05820 | D |  | 40310 | M05820 | CI# 40310 - P-513 - NSPI WO - U&U 15N Willow Lane Circuit Switch Additions (Q2 2013) - $435,680
M07589 | O |  | 40314 | M07589 | P-516 - (FIN) - CI #40314 - Main Computer Centre Upgrade - $7,807,740; Decreased spend amount ($584,790)
M06973 | O |  | 40320 | M06973 | P-128.15 - CI #40320 - Nova Scotia Power Inc. (NSPI) Work Order - Subsequent Approval Item - LED Streetlights - Capital Work Order and Tariff Application
M06049 | O |  | 40648 | M06049 | CI# 40648 - P-128.13 - NSPI WO - IT‐ Field Mobility System ‐ $3,332,514 - Outside Quarter - December 23, 2013
M07576 | D |  | 40868 | M07576 | P-516 - (FIN) - CI #40868 - 64V-T1 Transformer Replacement - $679,938; Decreased spend amount ($269,814)
M05106 | ?? |  | 40906 | M05106 | CI# 40906 - P-512 - NSPI WO - U&U Automatic Sleeve Replacement – $287,402
M05218 | G |  | 41126 | M05218 | CI# 41126 - P-128.12 - NSPI WO - HYD - Annapolis Sluiceway and Powerhouse Stop Log Refurbishment - $1,068,327
M06691 | G |  | 41130 | M06691 | CI# 41130 - P-128.14 - NSPI WO - HYD - Avon #2 Generator Stator Rewind - $633,484. ACE amount $694,096. $72,684 spent to date
M08786 | G |  | 41139 | M08786 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) - CI 41139 – HYD – Annapolis Sluiceway Superstructure Refurbishment – $3,041,862
M05067 | G |  | 41141 | M05067 | CI# 41141 - P-128.12 - NSPI WO - HYD - Sissiboo Grand Lake Spillway -
M06694 | G |  | 41142 | M06694 | CI# 41142 - P-128.15 - NSPI WO - HYD - St. Margaret's Bay - Sandy Lake Fish Passage - $3,926,079. ACE amount $3,433,314. $433,102 spent to date
M07804 | G |  | 41142 | M07804 | P-516 - CI # 41142 - HYD St. Margaret's Bay - Sandy Lake Fish Passage - $2,610,980
M05220 | G |  | 41228 | M05220 | CI# 41228 - P-128.12 - NSPI WO - TUC3 Turbine HP Impulse Blade Replacement - $1,633,539
M05065 | G |  | 41234 | M05065 | CI# 41234 - P-128.12 - NSPI WO - LIN4 Boiler Refurbishment -
M05064 | G |  | 41235 | M05064 | CI# 41235 - P-128.12 - NSPI WO - LIN1 Boiler Refurbishment
M05063 | G |  | 41248 | M05063 | CI# 41248 - P-128.12 - NSPI WO - TUC - Lube OIl Storage Building -
M06015 | G |  | 41265 | M06015 | CI# 41265 - P-128.13 - NSPI WO - TUC - Oil Dock Piling Refurbishment - (Q3 2013) - $610,664
M06352 | D |  | 41349 | M06352 | CI# 41349 - P-514 - NSPI WO - 2012 Off Road to Roadside (Q2 2014) - $1,381.102
M07577 | D |  | 41351 | M07577 | P-516 - (FIN) - CI #41351 - 2012 Distribution Automation - $270,944; Decreased spend amount ($283,021)
M05219 | O |  | 41403 | M05219 | CI# 41403 - P-128.12 - NSPI WO - GIS Enterprise License Agreement - $357,500
M07234 | O |  | 41425 | M07234 | P-128.16 - CI# 41425 - Nova Scotia Power Inc. (NSPI) WO - 2016 ACE Plan Capital Item for Subsequent Approval - Cognos Upgrade
M07579 | T&D | N | 41429 | M07579 | P-516 - (FIN) - CI #41429 - 2012 Substation PCB Equipment Removal - $1,282,337; Decreased spend amount ($572,328)
M06803 | O |  | 41432 | M06803 | CI# 41432 - P-128.14 - NSPI WO - ATO - L7009 Lidar Upgrades & Maintenance - $3,929,423. ATO Amount $986,614. $3,746,269 spent to date
M07580 | T&D |  | 41434 | M07580 | P-516 - (FIN) - CI #41434 - Procure Additional 42 MVA Spare Transformer- $716,221; Decreased spend amount ($327,764)
M07384 | D |  | 41437 | M07384 | CI #41437 - P-516 - Nova Scotia Power Inc. (NSPI) Kempt Rd Transformer ATO/FIN - $1,151,316; ATO amount $361,115
M07006 | T |  | 41438 | M07006 | P-128.15 - CI #41438 - NSPI WO - 2015 ACE Plan Capital Item for Subsequent Approval - 85S Cable Termination Replacement
M06350 | G |  | 41525 | M06350 | CI# 41525 - P-128.12 - NSPI WO - TRE 5 5-1 Pulveriser Refurbishment (Q2 2014) - $576,305
M05514 | D |  | 41534 | M05514 | CI# 41534 - P-128.12 - NSPI WO - 2012 Reliability Technologies Distribution - $1,040,175
M07460 | T | N | 41535 | M07460 | P-516 - CI# 41535 - NSPI WO - 2012 Steel Tower Protective Painting System - $1,701,691
M05105 | T |  | 41536 | M05105 | CI# 41536 - P-128.12 - NSPI WO - 2012 Reliability Technologies Transmission – $468,303
M05066 | T |  | 41537 | M05066 | CI# 41537 - P-128.12 - NSPI WO - Amherst 138kV Substation -
M06887 | D |  | 41672 | M06887 | CI# 41672 - P-514 - NSPI WO - Morris St./Water St. Underground U&U - $948,562. ATO amount $410,414.
M06219 | G |  | 41705 | M06219 | CI# 41705 - P-128.14 - NSPI WO - Q1 2014 - Milton Hydro Office Construction - $733,611
M04937 | D |  | 41797 | M04937 | CI# 41797 - P-128.12 - NSPI WO - Brier Island Crossing - $2,212,073
M06806 | D |  | 41797 | M06806 | CI# 41797 - P-128.14 - NSPI WO - ATO/FIN- Brier Island Crossing - $2,581,168. ATO amount $369,095
M05512 | G |  | 41843 | M05512 | CI# 41843 - P-512 - NSPI WO - TUC2 U&U HP/IP Blades Replacement - $4,056,204
M07555 | G |  | 41988 | M07555 | P-516 - CI #41988 - FIN - NSPI Work Order - HYD - U&U Big Falls #5 Overhaul - $1,008,398; Decreased spend amount ($343,207)
M05416 | G |  | 42127 | M05416 | CI# 42127 - P-128.13 - NSPI WO - South Canoe Wind Project - $93,091,536
M05582 | G |  | 42648 | M05582 | CI# 42648 - P-128.13 - NSPI WO - HYD Harmony Fish Ladder - Outside Quarter March 13, 2013 - $821,334
M06351 | G |  | 42666 | M06351 | CI# 42666 - P-514 - NSPI WO - HYD-Tusket #2 Overhaul (Q2 2014) - $1,116,199
M05212 | G |  | 42868 | M05212 | CI# 42868 - P-512 - NSPI WO - U&U Jordan Lake Diversion Refurbishment - $780,299
M05214 | G |  | 42907 | M05214 | CI# 42907 - P-512 - NSPI WO - CT U&U Burnside FT Overhaul - $2,490,181
M06050 | G |  | 42982 | M06050 | CI# 42982 - P-128.13 - NSPI WO - TUC6 Gland Steam System Improvements ‐ $1,308,372 - Outside Quarter - December 23, 2013
M05215 | G |  | 42991 | M05215 | CI# 42991 - P-512 - NSPI WO - TUC3 U&U Turbine IP/LP Refurbishment - $1678,031
M05949 | G |  | 43008 | M05949 | CI# 43008 - P-128.13 - NSPI - WO - TRI5 Turbine - Generator Fire Protection - Outside Quarter October 30, 2013 - $305,358
M07297 | G |  | 43027 | M07297 | CI# 43027 - P-128.15 - NSPI WO - POT - Refurbish Dust Collection Area Explosion System - 2015 ACE Plan Item Less than $250 Thousand
M06136 | G |  | 43067 | M06136 | CI# 43067 - P-128.14 - NSPI WO - HYD - Cheticamp Dam D-1 Refurbishment - Outside Quarter March 4, 2014 - $5,778,847
M07235 | G |  | 43088 | M07235 | P-515 - CI# 43088 - NSPI WO - ATO - LIN3 Generator Rotor Rewind
M05213 | G |  | 43089 | M05213 | CI# 43089 - P-512 - NSPI WO - POT U&U Safety Eyewash and Shower - $275,509
M05209 | D |  | 43106 | M05209 | CI# 43106 - P-512 - NSPI WO - U&U 126H-311 Porters Lake Targeted Replacements - $405,095
M05388 | G |  | 43116 | M05388 | CI# 43116 - P-512 - NSPI WO - TRE5 U&U 5-1 and 5-2 CW Pump Refurbishments - $400,978
M05511 | G |  | 43121 | M05511 | CI# 43121 - P-512 - NSPI WO - TRE5 U&U Turbine Repairs - $3,374,762
M07581 | D |  | 43126 | M07581 | P-516 - (FIN) - CI #43126 - 13V-303 Bear River Targeted Feeder Replacements - $418,617; Decreased spend amount ($380,360)
M07065 | G |  | 43128 | M07065 | CI# 43128 - Nova Scotia Power Inc. (NSPI) WO - Scope Change Capital Item - HYD GIS Gearbox and Bearing Replacement
M07985 | G |  | 43128 | M07985 | P-517 - Nova Scotia Power Inc. (NSPI) -CI 43128 – (ATO) - HYD Gisborne Gearbox and Bearing Replacement – $829,447
M07237 | G |  | 43136 | M07237 | P-515 - CI# 43136 - NSPI WO - ATO - HYD Weymouth Unit #1 Headcover Replacement
M05822 | G |  | 43165 | M05822 | CI# 43165 - P-128.13 - NSPI WO - LIN4 Boiler Refurbishment (Q2 2013) - $450,134
M05821 | G |  | 43166 | M05821 | CI# 43166 - P-128.13 - NSPI WO - LIN Mill Refurbishment (Q2 2013) - $544,692
M05210 | D |  | 43176 | M05210 | CI# 43176 - P-512 - NSPI WO - U&U 19W-312G Argyle Sound Targeted Replacements - $522,333
M05387 | T |  | 43187 | M05387 | CI# 43187 - P-512 - NSPI WO - U&U L8002 Tower Refurbishment - $370,190
M07853 | O |  | 43202 | M07853 | P-128.17 - Nova Scotia Power (NSPI) - CI 43202 Replace Mobile Radio System (2017) - $6,296,878 (Partially Confidential)
M08100 | T |  | 43205 | M08100 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 43205 - L5510 Insulator Replacements - $2,908,944
M07582 | T&D | N | 43231 | M07582 | P-516 - (FIN) - CI #43231 - 2013 Substation PCB Equipment Removal - $797,063; Decreased spend amount ($699,562)
M07583 | T&D | N | 43237 | M07583 | P-516 - (FIN) - CI #43237 - 2013 Substation Recloser Replacements - $1,126,614; Decreased spend amount ($736,764)
M08784 | G |  | 43260 | M08784 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) - CI 43260 – 2013 Transmission Line Insulator Replacements – $303,626
M06053 | D |  | 43278 | M06053 | CI# 43278 - P-128.13 - NSPI WO - Halifax 4kV Conversion – Part 1 ‐ $275,390 - Outside Quarter - December 23, 2013
M06016 | D |  | 43286 | M06016 | CI# 43286 - P-128.13 - NSPI WO - 6S Terrace Street Conversion Phase 1 - (Q3 2013) - $1,196,401
M05216 | G |  | 43290 | M05216 | CI# 43290 - P-512 - NSPI WO - TUC3 U&U Turbine Control Valves Refurbishment - $422,357
M06294 | T |  | 43291 | M06294 | CI# 43291 - P-128.14 - NSPI WO - Protection Risk Reduction 67N-Onslow 230KV - Outside the Quarter - June 25, 2014 - $2,870,285
M06975 | T |  | 43291 | M06975 | CI# 43291 - P-514 - NSPI WO - Protection Risk Reduction 67N-Onslow 230kV - $3,448,979. ATO amount $578,694. $2,410,524 spent to date
M06660 | T |  | 43324 | M06660 | CI# 43324 -P-128.15 NSPI WO - Replace L-6513 / Upgrade Line Terminals
M05386 | G |  | 43326 | M05386 | CI# 43326 - P-512 - NSPI WO - TUC3 U&U HP Feedwater Piping Replacement - $597,883
M07382 | G |  | 43389 | M07382 | CI# 43389- P-128.15 - Nova Scotia Power Inc. (NSPI) - NSPI WO - LIN3 Bentley Nevada Upgrade - System 1 - $298,363; ACE amount $242,907; Project is complete. - 2015 ACE Plan Capital Items Less than $250 Thousand
M05580 | G |  | 43419 | M05580 | CI# 43419 - P-513 - NSPI WO - TUC2 U&U FD Fan Bearings Replacement - Outside Quarter March 13, 2013 - $616,712
M06137 | D |  | 43427 | M06137 | CI# 43427 - P-514 - NSPI WO - U &U - 62N 510 Breaker and Control Replacement - Outside Quarter March 4, 2014 - $520,123
M06051 | O |  | 43467 | M06051 | CI# 43467 - P-128.13 - NSPI WO - Plant Wireless Infrastructure ‐ $940,027 - Outside Quarter - December 23, 2013
M05211 | G |  | 43469 | M05211 | CI# 43469 - P-512 - NSPI WO - U&U Raynard's Lake Fish Ladder - $476,757
M09346 | T |  | 43490 | M09346 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI 43490‐ Steel Tower Life Extension – (FIN) Decrease in costs by $607,948 (2019 Q2)
M06017 | D |  | 43548 | M06017 | CI# 43548 - P-128.13 - NSPI WO - 533S Mason Street Conversion - (Q3 2013) - $720,901
M07236 | D |  | 43672 | M07236 | P-515 - CI #43672 - NSPI WO - ATO - 82V-T1 (Elmsdale) Transformer Rewind
M06111 | T | N | 43681 | M06111 | CI# 43681 - P-128.14 - NSPI WO - South Canoe Wind Project Network Upgrades - $4,650,955 - Outside Quarter - December 23, 2013
M08958 | G |  | 43681 | M08958 | P-518 - Nova Scotia Power Inc. (NSPI) - (FIN) CI 43681 ‐ South Canoe Wind Project Substation Network Upgrades – $4,270,258
M06112 | G |  | 43683 | M06112 | CI# 43683 - P-128.14 - NSPI WO - South Canoe Wind Project Transmission Line - $5,831,002 - Outside Quarter - December 23, 2013
M08959 | G |  | 43683 | M08959 | P-518 - Nova Scotia Power Inc. (NSPI) - (FIN) CI 43683 ‐ South Canoe Wind Project (SCWP) Transmission Line – $5,179,767
M06054 | G |  | 43684 | M06054 | CI# 43684 - P-128.14 - NSPI WO - Interconnection Substation South Canoe Wind Project ‐ $7,760,891 - Outside Quarter - December 23, 2013
M06052 | D |  | 43726 | M06052 | CI# 43726 - P-128.13 - NSPI WO - Replace 3N‐T51 Transformer ‐ $1,109,247 - Outside Quarter - December 23, 2013
M07584 | D |  | 43726 | M07584 | P-516 - (FIN) - CI #43726 - Replace 3N-T51 Transformer - $825,136; Decreased spend amount ($284,111)
M05385 | T&D |  | 43750 | M05385 | CI# 43750 - P-512 - NSPI WO - U&U 22W Barrington Passage Project - $404,531
M05650 | T |  | 43786 | M05650 | CI# 43786 - P-128.13 - NSPI WO - 2013 L8002 Tower Refurbishments (Q1 2013) - $2,170,668
M07238 | T |  | 43786 | M07238 | P-515 - CI #43786 - NSPI WO - ATO/Scope Change Capital Item - 2013 L8002 Tower Refurbishments
M05384 | G |  | 43826 | M05384 | CI# 43826 - P-512 - NSPI WO - U&U HYD Annapolis Powerhouse Roof Hatch Replacement - $432,723
M06047 | G |  | 43906 | M06047 | CI# 43906 - P-513 - NSPI WO - TUC4 U&U LM6000 Engine Refurbishment ‐ $4,214,899 and CI#45630 - TUC4 U&U LM6000 Rotable Engine Purchase - $6,612,813 - Outside Quarter December 23, 2013
M05818 | G |  | 44027 | M05818 | CI# 44027 - P-513 - NSPI WO - TUC2 U&U High Pressure Nozzles Replacement (Q2 2013) - $598,090
M06014 | G |  | 44027 | M06014 | CI# 44027 - P-513 - NSPI WO - TUC2 U&U Turbine High Pressure Nozzles Replacement - (Q3 2013) - $606,235
M05947 | G |  | 44030 | M05947 | CI# 44030 - P-513 - NSPI - WO - International Coal Pier - Outside Quarter October 30, 2013 - $6,589,506
M05648 | G |  | 44046 | M05648 | CI# 44046 - P-513 - NSPI WO - TUC2 U&U HP/IP Stationary Seals Replacement (Q1 2013) - $506,150
M05817 | G |  | 44047 | M05817 | CI# 44047 - P-513 - NSPI WO - TUC2 Turbine LP Row 6 LH & RH Blades Refurbishment (Q2 2013) - $922,545
M05513 | G |  | 44066 | M05513 | CI# 44066 - P-512 - NSPI WO - LIN4 U&U Breach Repairs - $271,301
M05581 | G |  | 44086 | M05581 | CI# 44086 - P-513 - NSPI WO - TRE5 U&U 504 Mill Refurbishment - Outside Quarter March 13, 2013 - $597,055
M07763 | G |  | 44188 | M07763 | P-516 - CI 44188 - TRE - Ash Site Phase 1 Capping - $5,011,659
M08055 | G |  | 44188 | M08055 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 44188 ‐ TRE ‐ Ash Site Phase 1 Capping – $5,028,580
M05816 | G |  | 44247 | M05816 | CI# 44247 - P-513 - NSPI WO - TUC2 U&U Turbine Control Valves (Q2 2013) - $717,053
M06135 | G |  | 44248 | M06135 | CI# 44248 - P-128.14 - NSPI WO - HYD MAcMillan D-7 Spillway Refurbishment - Outside Quarter - March 4, 2014 - $ 5,279,936
M05815 | G |  | 44266 | M05815 | CI# 44266 - P-513 - NSPI WO - TRE5 U&U Mill Refurbishment (Q2 2013) - $594,552
M06013 | G |  | 44266 | M06013 | CI# 44266 - P-513 - NSPI WO - TRE5 U&U 5-2 Mill Refurbishment - (Q3 2013) - $610,664
M08180 | G |  | 44267 | M08180 | P-517 - Nova Scotia Power Inc. (NSPI) (ATO) - CI 44267 – TRE Ash Lagoon Site Closure – $9,568,879
M06216 | G |  | 44294 | M06216 | CI# 44294 - P-514 - NSPI WO - Q1 2014 - HYD - U&U Mill Lake Unit#2 Refurbishment - $516,830
M06804 | G |  | 44294 | M06804 | CI# 44294 - P-514 - NSPI WO - ATO- HYD - U&U Mill Lake Unit #2 Refurbishment - $902,930. ATO amount $386,100. $902,930 dollars spent to date.
M05649 | G |  | 44426 | M05649 | CI# 44426 - P-513 - NSPI WO - HYD U&U Weymouth #2 Headcover Replacement (Q1 2013) - $619,126
M06012 | O |  | 44446 | M06012 | CI# 44446 - P-513 - NSPI WO - IT U&U Windows 7 Migration - (Q3 2013) - $704,437
M05819 | G |  | 44592 | M05819 | CI# 44592 - P-513 - NSPI WO - TUC1 U&U Generator Terminal Bushing Seals Replacement (Q2 2013) - $580,917
M07378 | G |  | 44595 | M07378 | CI# 44595 - P-128.16 - Nova Scotia Power Inc. (NSPI) - Hollow Bridge Canal & Intake - $4,257,638, ACE amount $3,137,002
M07857 | G |  | 44595 | M07857 | P-517 - Nova Scotia Power (NSPI) - CI 44595 – HYD – Hollow Bridge Canal and Intake Refurbishment – $4,600,336
M06971 | G |  | 44669 | M06971 | CI# 44669 - P-128.14 - NSPI WO - HYD Wreck Cove Fire Suppression Upgrades - $1,034,915. ACE Amount $333,589; $87,416 spent to date
M07662 | G |  | 44669 | M07662 | P-516 - CI #44669 - Nova Scotia Power Inc. (NSPI) WO - HYD Wreck Cove Fire Suppression Upgrades - ATO - $1,767,125 - Variance $732,210
M07662 | G |  | 44669 | M07662 | P-516 - CI #44669 - Nova Scotia Power Inc. (NSPI) WO - HYD Wreck Cove Fire Suppression Upgrades - ATO - $1,767,125 - Variance $732,210
M07746 | O |  | 44671 | M07746 | P-128.16 - Nova Scotia Power Inc. (NSPI) CI# 44671 - Enterprise Resource Planning Application (ERP) $89,664,000 - P-516
M07746 | O |  | 44671 | M07746 | P-128.16 - Nova Scotia Power Inc. (NSPI) CI# 44671 - Enterprise Resource Planning Application (ERP) $89,664,000 - P-516
M05948 | O |  | 44712 | M05948 | CI# 44712 - P-513 - NSPI - WO - IT U&U Oracle Licensing Migration - $1,340,608 - Outside Quarter October 30, 2013
M08052 | G |  | 44716 | M08052 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 44716 ‐ TUC2 North Boiler Feedwater Pump Refurbishment – $274,951
M09438 | G |  | 44716 | M09438 | P-519 - Nova Scotia Power Inc. (NSPI) -CI 44716 - TUC2 North Boiler Feedwater Pump Refurbishment - $771,125
M08359 | T |  | 44749 | M08359 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 44749 - Tiverton Tower Replacement - $1,465,132 - 3rd Quarter 2017
M09206 | T |  | 44749 | M09206 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 44749 - 509V-301 – Tiverton Tower and Crossing Replacement – $1,954,524 (ATO)
M07659 | G |  | 44775 | M07659 | P-128.16 - CI #44775 - Nova Scotia Power Inc. (NSPI) WO -TUC4 LM6000 Generator Stator Re-wedge
M07659 | G |  | 44775 | M07659 | P-128.16 - CI #44775 - Nova Scotia Power Inc. (NSPI) WO -TUC4 LM6000 Generator Stator Re-wedge
M08099 | G |  | 44776 | M08099 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 44776 - TUC#5 LM6000 Generator Stator Re-Wedge - $1,361,301
M07231 | D |  | 44836 | M07231 | P-128.15 - CI #44836 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - Halifax 4kV Conversion Part 2
M07554 | G |  | 44887 | M07554 | P-516 - CI #44887 - FIN - NSPI Work Order - HYD-Sissiboo Pipeline Replacement- $955,600; ATO amount $480,518
M06805 |  |  | 44975 | M06805 | CI# 44975 - P-128.14 - NSPI WO - ATO- Sacrificial Anode Installation Program Phase 1 - $815,277. ATO Amount $525,230. $744,167 dollars spent to date.
M07007 | G |  | 44978 | M07007 | P-128.15 - CI #44978 - NSPI WO - 2015 ACE Plan Capital Item for Subsequent Approval - HYD Wreck Cove Controls Upgrade
M06505 | T |  | 44984 | M06505 | CI# 44984 - P-128.14 - NSPI WO (Q3 2014) - 9C Aberdeen Line Tap - $834,595; ACE amount $846,755. Zero dollars spent to date. - Third Quarter Capital Item
M07055 | T |  | 44987 | M07055 | P-128.15 - CI #44987 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - L7003 Lidar Upgrades
M06844 | T |  | 45066 | M06844 | CI # 45066-P-128.15 - NSPI WO- Upgrade L6511 and L7019 Thermal Rating - NSPI WO - NS Power Maritime Link-Related Transmission Capital Work - Subsequent Approval Item
M06525 | T |  | 45067 | M06525 | P-128.14 - CI # 45067 - 67N Onslow 345 KV Node Swap - NSPI WO - Subsequent Approval Item.
M06044 | G |  | 45086 | M06044 | CI# 45086 - P-513 - NSPI WO - POT U&U - Turbine Blade Replacements - $1,190,511 - Outside Quarter December 23, 2013
M06692 | O |  | 45106 | M06692 | CI# 45106 - P-128.14 - NSPI WO - IT - Printer Fleet Refresh - $349,026. ACE amount $500,000. $341,307 spent to date
M06045 | G |  | 45115 | M06045 | CI# 45115 - P-513 - NSPI WO - HYD U&U Nictaux Plant Automation - $446,296 - Outside Quarter December 23, 2013
M06799 | G |  | 45171 | M06799 | CI# 45171 - P-128.15 - NSPI WO - HYD Avon #1 Pipeline Replacement - $1,012,419. ACE amount $547,780. $30,340 dollars spent to date.
M06046 | G |  | 45269 | M06046 | CI# 45269 - P-513 - NSPI WO - CT U&U Tusket Engine Replacement ‐ 2,089,591 - Outside Quarter December 23, 2013
M07008 | T&D |  | 45306 | M07008 | P-128.15 - CI #45306 - NSPI WO - 2015 ACE Plan Capital Item for Subsequent Approval - Prime Brook Substation Addition
M07381 | G |  | 45330 | M07381 | CI# 45330- P-128.14 - Nova Scotia Power Inc. (NSPI) - HYD Culvert Replacement - $660,123; ACE amount $116,396;
M06564 | G |  | 45392 | M06564 | CI# 45392 - P-128.14 - NSPI WO - TRE Bunker C System Upgrades - $469,838 - ACE Amount $288,886. Outside the Quarter - December 2, 2014. $21,825 spent to date.
M07504 | G |  | 45392 | M07504 | CI# 45392 - P-516 - Nova Scotia Power Inc. (NSPI) - ATO - TRE Bunker C System Upgrades - $889,838; ATO amount $420,000; $889,838 spent as at April 30, 2016. This project is complete; final invoice ongoing.
M06138 | G |  | 45592 | M06138 | CI# 45592 - P-514 - NSPI WO - TUC3 - U & U Turbine - IP Row 2 Blading Phase 1 - Outside Quarter March 4, 2014 - $506,816
M06348 | G |  | 45611 | M06348 | CI# 45611 - P-514 - NSPI WO - LIN U&U Heavy Oil Recirculation Line Refurbishment (Q2 2014) - $1,304,395
M06048 | G |  | 45630 | M06048 | CI# 45630 - P-513 - NSPI WO - TUC4 U&U LM6000 Rotable Engine Purchase - $6,612,813 - Outside Quarter December 23, 2013
M06091 | G |  | 45670 | M06091 | CI# 45670 - P-513 - NSPI WO - LIN3 U&U SH#5 Tube Refurbishments (Q4 2013) - $338,216
M06560 | G |  | 45733 | M06560 | CI# 45733 - P-514 - NSPI WO - CT Burnside Unit #3 Generator Refurbishment U&U - $2,567,808 - Outside the Quarter - December 2, 2014. $1,618,270 spent to date.
M07056 | T |  | 45795 | M07056 | P-128.15 - CI #45795 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - L6503 Replacements
M06561 | G |  | 45802 | M06561 | CI# 45802 - P-514 - NSPI WO - LIN E-Gallery Floor Replacement U&U - $950,629 - Outside the Quarter - December 2, 2014. $94,017 spent to date.
M06885 | G |  | 45802 | M06885 | CI# 45802 - P-514 - NSPI WO - LIN E-Gallery Floor Replacement U&U - $2,365,470. ATO amount $1,414,841. $985,827 spent to date - Q1 - 2015
M06217 | G |  | 45816 | M06217 | CI# 45816 - P-514 - NSPI WO - Q1 2014 - TUC3 U&U Turbine IP Row 21 Blading Phase 2 - $1,150,115
M08735 | G |  | 45816 | M08735 | P-518 - Nova Scotia Power Inc. (NSPI) - CI 45816 – TUC3 U&U Turbine - IP Row 21 Blading Phase 2 – $856,230 (FIN)
M06218 | G |  | 45876 | M06218 | CI# 45876 - P-514 - NSPI WO - Q1 2014 - TUC3 U&U Generator Refurbishment - $1,500,239
M08827 | G |  | 45876 | M08827 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) CI# 45876 - TUC3 - U&U Generator Refurbishment - $1,217,217
M06501 | O |  | 45881 | M06501 | CI# 45881 - P-514 - NSPI WO (Q3 2014) - IT Windows Server 2003 Upgrade P & A - $2,242,271. $206,538 spent to date
M07590 | O |  | 45881 | M07590 | P-516 - (FIN) - CI #45881 - IT - P&A - Windows Server 2003 Upgrade - $1,912,279; Decreased spend amount ($318,995)
M07003 | D |  | 45882 | M07003 | P-514 - CI # 45882 - NSPI WO - U&U - 103H-T63 Transformer Replacement
M09347 | D |  | 45882 | M09347 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 45882 - 103H-T63 Transformer Replacement U & U – (FIN) Decrease in costs by $304,266
M06502 | G |  | 45958 | M06502 | CI# 45958 - P-514 - NSPI WO (Q3 2014) - HYD - Nictaux Rotor Rewind U & U - $413,143. $127,445 spent to date
M06562 | G |  | 46065 | M06562 | CI# 46065 - P-514 - NSPI WO - HYD - Tom's Lake Spillway Refurbishment U&U - $612,312 - Outside the Quarter - December 2, 2014. $25,880 spent to date.
M07009 | G |  | 46068 | M07009 | P-128.15 - CI #46068 - NSPI WO - 2015 ACE Plan Capital Item for Subsequent Approval - LIN CW Debris Removal System
M07296 | O |  | 46073 | M07296 | CI# 46073 - P-128.16 - NSPI WO - IT - Lotus Notes/Oracle Application Replacement -Nova Scotia Power Inc. - 2016 ACE Plan Item for Subsequent Approval
M06563 | G |  | 46111 | M06563 | CI# 46111 - P-514 - NSPI WO - TRE 5 5-2 Boiler Feedwater Pump Refurbishment P & A - $474,925 - Outside the Quarter - December 2, 2014. $91,355 spent to date.
M06504 | G |  | 46171 | M06504 | CI# 46171 - P-514 - NSPI WO (Q3 2014) - Paradise Bearing Replacement U & U - $349,957. $186,354 spent to date. The bearings, temperature sensors and the control system have been replaced.
M07500 | G |  | 46191 | M07500 | CI# 46191 - P-128.16 - Nova Scotia Power Inc. (NSPI) - Tusket Fuel System Upgrade - $1,952,408; ACE amount $892,178; $288,171 spent as at April 30, 2016
M06800 | G |  | 46232 | M06800 | CI# 46232 - P-128.15 - HYD White Rock Pipeline Replacement - $685,805. Ace Amount $538,454. $26,215 dollars spent to date
M07298 | G |  | 46256 | M07298 | CI# 46256 - P-516 - NSPI WO - POT - Boiler Refurbishment 2015 - ATO
M06349 | G |  | 46294 | M06349 | CI# 46294 - P-514 - NSPI WO - HYD U&U WRC Unit 1 Stator Repair - (Q2 2014) - $366,027
M06798 | G |  | 46300 | M06798 | CI# 46300 - P-128.15 - NSPI WO - TRE6 - Air Heater Refurbishment - $2,040,366; ACE amount $752,215. Zero dollars to date.
M07057 | T |  | 46332 | M07057 | P-128.15 - CI #46332 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - L6539 Replacements
M07060 | T |  | 46333 | M07060 | P-128.15 - CI #46333 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - L6538 Replacements
M07986 | G |  | 46352 | M07986 | P-517 - Nova Scotia Power Inc. (NSPI) - (ATO) - CI 46352 – TRE5 Air Heater Refurbishment – $1,088,844
M07010 |  |  | 46356 | M07010 | P-128.15 - CI #46356 - NSPI WO - ATO - 2015 Sacrificial Anode Program
M07383 | T |  | 46360 | M07383 | CI# 46360 - P-128.16 - Nova Scotia Power Inc. (NSPI) - L5545B Reconductor - $820,437; ACE amount $202,492; $33,444 spent as at February 29, 2016 - 2016 ACE Plan Capital Items Less than $250 Thousand
M07656 | G |  | 46374 | M07656 | P-516 - CI #46374 - Nova Scotia Power Inc. (NSPI) WO - POT East CW Pump Refurbishment - U&U - $310,214
M07656 | G |  | 46374 | M07656 | P-516 - CI #46374 - Nova Scotia Power Inc. (NSPI) WO - POT East CW Pump Refurbishment - U&U - $310,214
M06883 | D |  | 46398 | M06883 | CI# 46398 - P-128.15 - NSPI WO - 20H Spryfield Voltage Conversion - $480,510. ACE amount $444,970. $218,831 spent to date
M06802 | G |  | 46411 | M06802 | CI# 46411 - P-128.15 - NSPI WO Hydro Asset Management Implementation - $590,884. ACE Amount $376,637. $107,947 dollars spent to date
M06974 | G |  | 46422 | M06974 | CI# 46422 - P-128.15 - NSPI WO - POT Automatic Trash Rack Cleaning System $329,721. ACE amount $233,741. Zero dollars spent to date
M07061 | G |  | 46432 | M07061 | P-515 - CI# 46432 - Nova Scotia Power Inc. (NSPI) WO - LIN U&U Coal System Refurbishment
M07927 | G |  | 46499 | M07927 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan CI for Subsequent Approval - CI# 46499 – Stator Rewind Kit Capital Spare – $2,871,003
M07300 | G |  | 46505 | M07300 | CI# 46505 - P-516 - NSPI WO - TUC2 U&U Low Pressure Row 6 Blade 75 Replacement
M08638 | G |  | 46505 | M08638 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) CI# 46506 - TUC Noise Monitoring System - $319,894 (Outside Quarter)
M06801 | G |  | 46507 | M06801 | CI# 46507 - P-128.15 - LM6000 - Fuel Nozzle Rotable Kit - $293,315. ACE Amount $295,772. Zero dollars spent to date.
M08785 | T |  | 46513 | M08785 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) - CI 46513 – 3C Port Hastings BPS Upgrade – $3,318,316
M07099 | O |  | 46552 | M07099 | P-128.15 - CI# 46552 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - Backbone Communication System Upgrade
M06884 | D | N | 46586 | M06884 | CI# 46586 - P-128.15 - NSPI WO - 2015 Substation Polychlorinated Biphenyl (PCB) Equipment Removal Program - $1,236,351. ACE amount $1,262,087. Zero dollars spent to date
M06972 | D |  | 46593 | M06972 | CI# 46593 - P-128.15 - NSPI WO - 70V-311 Bridgetown Voltage Conversion $534,887. ACE Amount $237,679. Zero spent to date
M07160 | D |  | 46651 | M07160 | CI# 46651 - P-128.15 - NSPI WO - 23H - Rockingham Voltage Conversion - Phase 1 - Subsequent Approval Item - Nova Scotia Power Inc.
M07281 | O |  | 46671 | M07281 | CI# 46671 -P-128.16 - NSPI WO - NERC CIP Version 5 Implementation -Nova Scotia Power Inc. - 2016 ACE Plan Item for Subsequent Approval
M06689 | G |  | 46713 | M06689 | CI# 46713 - P-514 - NSPI WO - TUC5 LM6000 - Engine 191-332 Refurbishment - P & A - $7,768,463. $3,029,959 spent to date
M07100 | O |  | 46739 | M07100 | P-128.15 - CI# 46739 - Nova Scotia Power Inc. (NSPI) WO - 2015 ACE Plan Capital Item for Subsequent Approval - IT - Outage Map Technology Upgrade
M06797 | G |  | 46791 | M06797 | CI# 46791 - P-515 - NSPI WO - HYD - Annapolis Runner Refurbishment U&U - $526,329. $454,958 spent to date. Refurbishment work has been completed. The reassembling of this unit it outstanding
M07549 | D |  | 46811 | M07549 | P-128.16 - CI #46811 - Nova Scotia Power Inc. (NSPI) WO - 2H Armdale Transformer Addition - $2,566,861; ACE amount $2,545,596; $9,298 spent as at May 31, 2016
M06796 | G |  | 47052 | M06796 | CI# 47052 - P-515 - NSPI WO - LIN3 Superheater #5 Tube Replacement U&U - $483,895; Zero dollars spent to date
M08349 | O |  | 47124 | M08349 | P-516 - CI# 47124 - Nova Scotia Power Inc. (NSPI) - Advanced Meter Infrastructure (AMI) Project
M07767 | O |  | 47124 | M07767 | P-516 - CI 47124 - NSPI Work Order - Advanced Meter Infrastructure (AMI) Pilot in the amount of $8,274,738
M06970 | T |  | 47131 | M06970 | CI# 47131 - P-514 - NSPI WO - L8001 Steel Tower Replacement U&U - $928,377. $506,729 spent to date
M07385 | G |  | 47158 | M07385 | CI# 47158 - P-516 - Nova Scotia Power Inc. (NSPI) - TRE5 HEP Piping U&U - $1319,254; $313,818 spent as at February 29, 2016. This project is complete; final invoicing is ongoing.
M07295 | G |  | 47163 | M07295 | CI# 47163 - P-128.16 - NSPI WO - HYD - Tusket Controls Upgrade - Nova Scotia Power Inc. - 2016 ACE Plan Item for Subsequent Approval
M07380 | G |  | 47167 | M07380 | CI# 47167- P-128.16 - Nova Scotia Power Inc. (NSPI) - Sandy Lake Surge Tank - $2,955,458; ACE amount $1,358,796;
M07683 | G |  | 47172 | M07683 | P-516 - CI #47172 - Nova Scotia Power Inc. (NSPI) WO - HYD Tidewater Unit 1 Overhaul - ATO - $2,017,916 - Variance - $599,384
M07683 | G |  | 47172 | M07683 | P-516 - CI #47172 - Nova Scotia Power Inc. (NSPI) WO - HYD Tidewater Unit 1 Overhaul - ATO - $2,017,916 - Variance - $599,384
M06882 | G |  | 47276 | M06882 | CI# 47276 - P-514 - NSPI WO - LIN 3 - U&U Generator Stator Re-Wedge - $441,755. Zero dollars spent to date
M08144 | G |  | 47331 | M08144 | P-517 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 47331 - LM6000 191‐253 Engine Refurbishment – $1,023,342 (CI outside quarter package)
M07684 | G |  | 47332 | M07684 | P-516 - CI #47332 - Nova Scotia Power Inc. (NSPI) WO - HYD Methals Overhaul - ATO $2,380,900 Variance - $987,973
M07684 | G |  | 47332 | M07684 | P-516 - CI #47332 - Nova Scotia Power Inc. (NSPI) WO - HYD Methals Overhaul - ATO $2,380,900 Variance - $987,973
M08787 | G |  | 47396 | M08787 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) - CI 47396 – HYD ‐ Nictaux Powerhouse Dam Refurb ‐ $1,224,610
M07002 | G |  | 47400 | M07002 | P-514 - CI # 47400 - NSPI - LIN3 U&U 8th Stage Diaphragm & Spill Strip Replacement
M07657 | O |  | 47403 | M07657 | P-128.16 - CI #47403 - Nova Scotia Power Inc. (NSPI) WO - Load Research Sample Update - $440,453
M07657 | O |  | 47403 | M07657 | P-128.16 - CI #47403 - Nova Scotia Power Inc. (NSPI) WO - Load Research Sample Update - $440,453
M07063 | D |  | 47471 | M07063 | P-515 - CI #47471 - Nova Scotia Power Inc. (NSPI) WO - 131H-422G-East Uniacke Road Load Growth P&A
M07062 | G |  | 47476 | M07062 | P-515 - CI# 47476 - Nova Scotia Power Inc. (NSPI) WO - HYD Wreck Cove Tailrace Rockfall U&U
M07501 | O |  | 47477 | M07501 | CI# 47477 - P-128.16 - Nova Scotia Power Inc. (NSPI) - IT - Security Enhancements - Next Generation Firewall - $3,927,576; ACE amount $2,536,1820; $611,799 spent as at April 30, 2016
M07064 | G |  | 47494 | M07064 | P-515 - CI# 47494 - Nova Scotia Power Inc. (NSPI) WO - 16W-302 Lake George Neutral Replacement P&A
M07988 | G |  | 47506 | M07988 | P-517 - Nova Scotia Power Inc. (NSPI) - (FIN) - CI 47506 ‐ LIN CW Screen Refurbishment 2016 – $666,401
M08050 | G |  | 47531 | M08050 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 47531 ‐ TRE6 LP Turbine Diaphragm Tip Seal Replacement ‐ $1,704,784
M08736 | G |  | 47531 | M08736 | P-518 - Nova Scotia Power Inc. (NSPI) - CI 47531 – TRE6 LP Turbine Diaphragm Tip Seal Replacement – $1,784,152
M07293 | G |  | 47551 | M07293 | CI# 47551 - P-128.16 - NSPI WO - HYD - SHH Controls Upgrade -Nova Scotia Power Inc. - 2016 ACE Plan Item for Subsequent Approval
M07987 | G |  | 47552 | M07987 | P-517 - Nova Scotia Power Inc. (NSPI) - (ATO) - CI 47552 – TRE5 – Boiler Refurbishment 2016 – 2,429,444
M07928 | G |  | 47553 | M07928 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan CI for Subsequent Approval - CI 47553 – TRE6 Turbine Valve Refurbishment – $570,600
M08476 | G |  | 47597 | M08476 | P-518 - Nova Scotia Power Inc. (NSPI) - (ATO) - CI 47597 – TRE6 Bottom Ash Chain Replacement – $1,170,884
M07855 | G |  | 47600 | M07855 | P-128.16 - Nova Scotia Power (NSPI) - CI 47600 – TRE Asbestos Abatement (2016) – $2,096,391
M07984 | G |  | 47606 | M07984 | P-128.16 - Nova Scotia Power Inc. (NSPI) - CI 47606 ‐ TRE5 Sootblower Controls Upgrade ‐ $285,301
M07759 | G |  | 47613 | M07759 | P-128.16 - CI 47613 - PHB Boiler Refurbishment 2016 - $572,360
M07759 | G |  | 47613 | M07759 | P-128.16 - CI 47613 - PHB Boiler Refurbishment 2016 - $572,360
M07760 | G |  | 47614 | M07760 | P-128.16 - CI 47614 - PHB Fuel System Refurbishment 2016 - $290,634
M07760 | G |  | 47614 | M07760 | P-128.16 - CI 47614 - PHB Fuel System Refurbishment 2016 - $290,634
M07005 | T |  | 47631 | M07005 | P-514 - CI # 47631 - NSPI WO - U&U - Capacitor Bank Breaker Replacements]
M07929 | G |  | 47648 | M07929 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan Capital Items for Subsequent Approval - CI 47648 – HYD Lequille Pipeline Replacement – $1,121,253
M07973 | G |  | 47654 | M07973 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 47654 ‐ HYD ‐ Gulch Penstock & Surge Tank Replacement ‐ $4,970,542
M07989 | G |  | 47661 | M07989 | P-517 - Nova Scotia Power Inc. (NSPI) - (FIN) - CI 47661 ‐ POT – Asbestos Management 2016 ‐ $347,326
M07974 | G |  | 47682 | M07974 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 47682 ‐ HYD Lequille Switchgear Replacement ‐ $776,391
M08294 | G |  | 47687 | M08294 | P-517 - Nova Scotia Power Inc. (NSPI) (ATO) - CI 47687 – POT Boiler Chem Cleaner – $1,603,103 (Filed outside Quarter Package Sept. 2017)
M07161 | T&D |  | 47693 | M07161 | CI# 47693 - P-515- NSPI WO - 63V-313G-Evangeline Trail Reconductor P&A - Nova Scotia Power Inc.
M09508 | T |  | 47751 | M09508 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI 47751 – ECC - Dynamic Line Rating Implementation – $4,978,090
M07233 | D |  | 47753 | M07233 | P-128.16 - CI #47753 - Nova Scotia Power Inc. (NSPI) WO - 2016 ACE Plan Capital Item for Subsequent Approval - 24C-442GB Highway 16 Reconductor Phase 2
M07982 | D |  | 47756 | M07982 | P-128.16 - Nova Scotia Power Inc. (NSPI) - CI 47756 ‐ 36V‐303 Reconductor Middle Dyke Rd – $287,779
M07970 | D |  | 47760 | M07970 | P-128.17 - Nova Scotia Power Inc. (NSPI) -CI 47760 ‐ 85S‐402 Re‐Insulate – $1,551,859
M07159 | D |  | 47773 | M07159 | CI# 47773 - P-515 - NSPI WO - 3N - Oxford Conversion Phase 2 P&A - Nova Scotia Power Inc.
M07761 | D |  | 47776 | M07761 | P-128.17 - CI 47776 - 111S Prime Brook Feeder Exits & Feeders - $1,504,630 (Partially Confidential)
M08368 | D |  | 47786 | M08368 | P-128.16 - Nova Scotia Power Inc. (NSPI) - CI# 47786 - 129h Kearney Lake Rd Load Transfer - $286,280 - 3rd Quarter 2017
M08175 | D |  | 47787 | M08175 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 47787 – 2H Armdale New Feeders – $988,498 (2017 - filed outside quarter)
M09661 | D |  | 47787 | M09661 | P-520 - Nova Scotia Power Inc. (NSPI) - CI 47787 – 2H Armdale New Feeders – $1,734,221
M07301 | G |  | 47814 | M07301 | CI# 47814 - P-516 - NSPI WO - HYD - U&U WRC Evacuation Tunnel Upgrade
M08098 | G |  | 47874 | M08098 | P-128.16 - Nova Scotia Power Inc. (NSPI) - CI 47874 - LIN Ash Scale Replacement - $481,252
M07930 | G |  | 47876 | M07930 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan Capital Items for Subsequent Approval - CI 47876 – HYD Lequille Overhaul – $1,395,229
M08477 | G |  | 47876 | M08477 | P-518 - Nova Scotia Power Inc. (NSPI) - (ATO) - CI 47876 – HYD Lequille Overhaul – $2,170,697
M07856 | G |  | 47933 | M07856 | P-128.16 - Nova Scotia Power (NSPI) - CI 47933 – LIN4 Turbine Vibration Monitoring Upgrade – $280,095
M07299 | G |  | 47934 | M07299 | CI# 47934 - P-516 - NSPI WO - TUC3 U&U CW Piping Refurbishment
M08686 | T |  | 47950 | M08686 | P-518 - Nova Scotia Power Inc. (NSPI) - CI 47950 – L5017 Replacements and Upgrades ATO – $3,062,664
M07294 | G |  | 48020 | M07294 | CI# 48020 - P-128.16 - NSPI WO - HYD - Ruth Falls #3 Generator Refurbishment -Nova Scotia Power Inc. - 2016 ACE Plan Item for Subsequent Approval
M07571 | D |  | 48022 | M07571 | P-128.16 - CI #48022 - Spider Lake Substation - $6,839,528; Ace amount $6,348,981; $112,631 spent as at June 30, 2016
M09110 | D |  | 48022 | M09110 | P-519 - Nova Scotia Power Inc. (NSPI) - (ATO) CI 48022 – Spider Lake Substation Addition – $9,223,260
M07931 | G |  | 48052 | M07931 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan Capital Items for Subsequent Approval - CI 48052 – HYD Annapolis HVAC Upgrade – $1,573,596
M07158 | G |  | 48058 | M07158 | CI# 48058 - P-515 - NSPI WO- PTMT - Railcar Access Ramp U&U
M07550 | D |  | 48061 | M07550 | P-128.16 - CI #48061 - Nova Scotia Power Inc. (NSPI) WO - New Mobile Substation 7.5MVA - $2,390,744; ACE amount $1,728,234; $3,417 spent as at May 31, 2016
M07983 | T&D |  | 48111 | M07983 | P-128.16 - Nova Scotia Power Inc. (NSPI) - CI 48111 ‐ East Switch Upgrades 15S ‐ $304,379
M07661 | T |  | 48113 | M07661 | P-516 - CI #48113 - Nova Scotia Power Inc. (NSPI) WO - 2016 Steel Tower Refurbishment - ATO - $1,699,991 - Variance $667,413
M07661 | T | N | 48113 | M07661 | P-516 - CI #48113 - Nova Scotia Power Inc. (NSPI) WO - 2016 Steel Tower Refurbishment - ATO - $1,699,991 - Variance $667,413
M08054 | T |  | 48114 | M08054 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 48114 ‐ 2016 Steel Tower Life Extension – $1,465,712 (2017 Q1)
M07551 | D |  | 48152 | M07551 | P-128.16 - CI #48152 - Nova Scotia Power Inc. (NSPI) WO - 20H-Spryfield Voltage Conversion Phase II - $460,246; ACE amount $375,848; $396,131 spent as at May 31, 2016
M07801 | T&D |  | 48155 | M07801 | P-128.17 - CI # 48155 - 2016 SCADA Application Upgrade - $400,688 (Partially Confidential)
M07379 | G |  | 48157 | M07379 | CI# 48157- P-128.16 - NSPI WO - TUC Auxiliary Boiler - $3,478,421; ACE amount $2,822,565;
M07155 | G |  | 48194 | M07155 | CI# 48194 -P-515 - . NSPI WO - 88S Lingan 230kV Breaker Replacement - U&U - Nova Scotia Power Inc.
M07503 | G |  | 48194 | M07503 | CI# 48194 - P-516 - ATO - Nova Scotia Power Inc. (NSPI) - 88S-713 Lingan 230V Breaker Replacement - $4,477,103; ATO amount $504,740; $4,465,321 spent as at April 30, 2016. This project is complete; final invoice ongoing.
M07764 | G |  | 48194 | M07764 | P-516 - CI 48194 - 88S-713 Lingan 230kV Breaker Replacement - $4,478,737
M07658 | D |  | 48195 | M07658 | P-128.16 - CI #48195 - Nova Scotia Power Inc. (NSPI) WO - Halifax 4kV Conversion Phase 3
M07658 | D |  | 48195 | M07658 | P-128.16 - CI #48195 - Nova Scotia Power Inc. (NSPI) WO - Halifax 4kV Conversion Phase 3
M07758 | O |  | 48236 | M07758 | P-128.16 - CI 48236 - Customer Experience Self-Serve Development Phase 1 - $811,203
M07758 | G |  | 48236 | M07758 | P-128.16 - CI 48236 - Customer Experience Self-Serve Development Phase 1 - $811,203
M07802 | O |  | 48238 | M07802 | P-128.17 - CI # 48238 - Customer Billing Experience Improvements - $405,324
M07502 | O |  | 48254 | M07502 | CI# 48254 - P-128.16 - Nova Scotia Power Inc. (NSPI) - IT - Outage Communication Technology Capacity Improvement- $2,146,081; ACE amount $1,500,000; $779,109 spent as at April 30, 2016
M07302 | G |  | 48354 | M07302 | CI# 48354 - P-516 - NSPI WO - LIN1 U&U Burner Front Refurbishment
M08360 | G |  | 48396 | M08360 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 48396 - HYD Bridge Remediation - $677,591 - 3rd Quarter 2017
M07461 | O |  | 48411 | M07461 | P-516 - CI# 48411 - NSPI WO - Internet Explorer Upgrade - $409,685; $170,760 spent as at March 31, 2016
M07573 | G |  | 48438 | M07573 | P-516 - (U&U) - CI #48438 - LIN4 ID Fan Damper and VIV Replacement - $524,658; $447,532 spent as at June 30, 2016. Project is complete; final invoicing ongoing
M07386 | G |  | 48471 | M07386 | CI# 48471 - P-516 - Nova Scotia Power Inc. (NSPI) - TUC3 HEP Piping U&U - $313,287; $280,064 spent as at February 29, 2016. This project is complete; final invoicing is ongoing.
M08097 | G |  | 48514 | M08097 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 48514 - LIN U&U Coal Truck Scale - $308,468
M08956 | G |  | 48535 | M08956 | P-518 - Nova Scotia Power Inc. (NSPI) - (FIN) CI 48535 ‐ HYD Scragg Lake Dam and Spillway Refurbishment – $1,625,672
M07765 | D |  | 48610 | M07765 | P-516 - CI 48610 - 16N-301 Stewiacke - Load Transfer - $852,654
M07552 | O |  | 48633 | M07552 | P-128.16 - CI #48633 - Nova Scotia Power Inc. (NSPI) WO - IT Security Enhancement - Java Security- $548,032; ACE amount $2,536,182; $238,767 spent as at May 31, 2016
M07660 | O |  | 48635 | M07660 | P-128.16 - CI #48635 - Nova Scotia Power Inc. (NSPI) WO -IT - Security Enhancements - Endpoint Security - $813,587
M07660 | O |  | 48635 | M07660 | P-128.16 - CI #48635 - Nova Scotia Power Inc. (NSPI) WO -IT - Security Enhancements - Endpoint Security - $813,587
M08733 | G |  | 48791 | M08733 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 48791 – HYD - WRC Safety Standards Upgrades – $1,760,570
M07990 | G |  | 48811 | M07990 | P-517 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 48811 ‐ LIN4 Feedwater Heater Level Control Upgrade – $296,832
M08679 | O |  | 48837 | M08679 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 48837 – AMO Fleet Environmental Data Management – $423,356
M07975 | G |  | 48893 | M07975 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 48893 ‐ TUC3 IP Turbine Refurbishment ‐ $4,871,454
M08636 | G |  | 48893 | M08636 | P-518 - Nova Scotia Power Inc. (NSPI) - CI# 48893 - TUC3 IP Turbine Refurbishment (ATO) - $5,357,210 (Outside Quarter)
M08362 | G |  | 48913 | M08362 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 48913 - HYD Tusket Facility Repairs - $1,183,470 - 3rd Quarter 2017
M08363 | G |  | 48914 | M08363 | P-128.17 - Nova Scotia Power Inc. (NSPI) -CI# 48914 - HYD Malay Falls Facility Repairs - $1,034,045 - 3rd Quarter 2017
M07653 | G |  | 48951 | M07653 | P-516 - CI #48951 - Nova Scotia Power Inc. (NSPI) WO - LIN4 72" CW Condenser Pipe Replacement - U&U - $414,715
M07653 | G |  | 48951 | M07653 | P-516 - CI #48951 - Nova Scotia Power Inc. (NSPI) WO - LIN4 72" CW Condenser Pipe Replacement - U&U - $414,715
M07976 | G |  | 49039 | M07976 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49039 ‐ HYD Lequille Controls Upgrades ‐ $762,912
M07735 | O |  | 49043 | M07735 | P-516 - CI 49043 (U & U) - IT ‐ Contact Centre Telephony Infrastructure – $2,504,109
M07735 | O |  | 49043 | M07735 | P-516 - CI 49043 (U & U) - IT ‐ Contact Centre Telephony Infrastructure – $2,504,109
M07807 | G |  | 49061 | M07807 | P-516 - CI # 49061 - LM6000 191-443 Engine Refurbishment - $1,047,421
M09301 | O |  | 49093 | M09301 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI 49093 – IT - Security Operations Center (SOC) and Security Information Event Monitoring (SIEM) – $4,074,948
M07977 | G |  | 49111 | M07977 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49111 ‐ POT Air Heater Refurbishment ‐ $272,538
M08216 | T |  | 49132 | M08216 | P-517 - Nova Scotia Power Inc. (NSPI) (U&U) - CI 49132 – PTMT Dock Winching & Access Refurbishment – $416,998
M07508 | O |  | 49212 | M07508 | CI# 49212 - P-516 - Nova Scotia Power Inc. (NSPI) - U&U - IT - My Account Single Sign-On - $465,079; $274,332 spent as at April 30, 2016. Application development and testing is complete; security testing remains to be completed
M07507 | D |  | 49253 | M07507 | CI# 49253 - P-516 - Nova Scotia Power Inc. (NSPI) - U&U - 20V-T1 Transformer Replacement - $1,305,748; $192,402 spent as at April 30, 2016
M09002 | D |  | 49253 | M09002 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) - CI 49253 – U&U 20V‐T1 Transformer Replacement – $960,811
M08176 | T |  | 49273 | M08176 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49273 – BGT2 Engine Refurbishment – $2,170,157; ACE amount $1,019,832 (2017 filed outside quarter)
M07572 | D |  | 49311 | M07572 | P-128.16 - (P&A) - CI #49311 - 93V-312 Lower Saulnierville Conductor Overload - $549,642; $0 spent as at June 30, 2016
M08297 | G |  | 49316 | M08297 | P-517 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 49316 – TUC3 CEMS Replacement – $461,704 (Filed outside Quarter Package Sept. 2017)
M07650 | G |  | 49351 | M07650 | P-516 - CI #49351 - Nova Scotia Power Inc. (NSPI) WO - LIN4 LTSH1 Tube Replacement U&U
M07651 | G |  | 49415 | M07651 | P-516 - CI #49415 - Nova Scotia Power Inc. (NSPI) WO - LIN4 HP IP Seal Replacement - U&U - $531,485
M07651 | G |  | 49415 | M07651 | P-516 - CI #49415 - Nova Scotia Power Inc. (NSPI) WO - LIN4 HP IP Seal Replacement - U&U - $531,485
M07652 | G |  | 49416 | M07652 | P-516 - CI #49416 - Nova Scotia Power Inc. (NSPI) WO - LIN4 Generator Stator Re-wedge - U&U - $593,619
M07652 | G |  | 49416 | M07652 | P-516 - CI #49416 - Nova Scotia Power Inc. (NSPI) WO - LIN4 Generator Stator Re-wedge - U&U - $593,619
M08215 | T |  | 49433 | M08215 | P-517 - Nova Scotia Power Inc. (NSPI) (ATO) - CI 49433 – LIN1 SH5 Boiler Tube Replacements – $848,377; ATO amount $354,981;
M08096 | G |  | 49438 | M08096 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49438 - LIN A Gallery Floor Replacement - $591,761
M08295 | G |  | 49466 | M08295 | P-517 - Nova Scotia Power Inc. (NSPI) - (ATO) - CI 49466 – PTMT Dock and Inhaul Conveyor – $920,823 (Filed outside Quarter Package Sept. 2017)
M09509 | O |  | 49480 | M09509 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI 49480 – Data Centre Disaster Recovery – $6,335,162
M07654 | G |  | 49497 | M07654 | P-516 - CI #49497 - Nova Scotia Power Inc. (NSPI) WO - LIN4 Snout Ring Replacement - U&U
M07654 | G |  | 49497 | M07654 | P-516 - CI #49497 - Nova Scotia Power Inc. (NSPI) WO - LIN4 Snout Ring Replacement - U&U
M08177 | G |  | 49499 | M08177 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49499 – PHB Boiler Refurbishment 2017 – $593,740; ACE amount $484,730 (2017 - filed outside Quarter)
M07978 | G |  | 49538 | M07978 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49538 ‐ TRE6 Generator Rotor Flux Probe Installation ‐ $784,610
M08213 | G |  | 49551 | M08213 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49551 – TRE5 CEMS Replacement – $671,295
M08179 | G |  | 49553 | M08179 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49553 – TRE Asbestos Abatement 2017 – $728,886; ACE amount $226,451 (2017 filed outside the quarter)
M08779 | G |  | 49594 | M08779 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 49594 – LM6000 TUC5 Airhouse Upgrade – $980,668
M08826 | G |  | 49596 | M08826 | P-518 - Nova Scotia Power Inc. (NSPI) (FIN) CI# 49596 - HYD - Hells Gate 2 Overhaul - $1,134,326
M07932 | G |  | 49596 | M07932 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan Capital Items for Subsequent Approval - CI 49596 – HYD Hells Gate 2 Overhaul – $1,204,263
M07979 | G |  | 49598 | M07979 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49598 ‐ HYD Gisborne Switchgear Replacement ‐ $747,450
M07806 | G |  | 49605 | M07806 | P-516 - CI # 49605 - CT Burnside #3 Engine Refurbishment - $2,032,866
M07736 | D |  | 49611 | M07736 | P-516 - CI 49611 (Misc. Capital Items) - New Distribution Rights‐of‐Way Phase 1 – $2,215,397
M07736 | D |  | 49611 | M07736 | P-516 - CI 49611 (Misc. Capital Items) - New Distribution Rights‐of‐Way Phase 1 – $2,215,397
M07940 | G |  | 49632 | M07940 | P-517 - Nova Scotia Power Inc. (NSPI) - U&U - CI 49632 – HYD White Rock Canal Refurbishment – $590,670
M07941 | G |  | 49633 | M07941 | P-517 - Nova Scotia Power Inc. (NSPI) - U&U - CI 49633 – HYD Trout River Lake Canal Refurbishment – $519,531
M08957 | G |  | 49633 | M08957 | P-518 - Nova Scotia Power Inc. (NSPI) - (FIN) CI 49633 ‐ HYD Trout River Lake Canal Refurbishment – $165,818
M09037 | G |  | 49666 | M09037 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 49666 – TUC1 South Boiler Feedwater Pump Refurbishment – $585,260 (U&U)
M07935 | G |  | 49674 | M07935 | P-128.17 - Nova Scotia Power Inc. (NSPI) - 2017 ACE Plan Capital Items for Subsequent Approval - CI 49674 – TUC2 Boiler Selective Waterwall Tube Replacements – $421,518
M08292 | G |  | 49693 | M08292 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49693 – TUC HFO Tank Dyke Piping Refurbishments – $664,753 (Filed outside Quarter Package 2017)
M08637 | G |  | 49707 | M08637 | P-518 - Nova Scotia Power Inc. (NSPI) - CI# 49707 - TUC2 Generator Bushing Replacement ATO - 956,939 (Outside Quarter)
M07685 | G |  | 49751 | M07685 | P-516 - CI #49751 - Nova Scotia Power Inc. (NSPI) WO - TUC1 LP Blading Refurbishment U&U - ATO $709,259
M07685 | G |  | 49751 | M07685 | P-516 - CI #49751 - Nova Scotia Power Inc. (NSPI) WO - TUC1 LP Blading Refurbishment U&U - ATO $709,259
M08634 | T |  | 49778 | M08634 | P-518 - Nova Scotia Power Inc. (NSPI) - CI# 49778 - L5535 Replacements and Upgrades (ATO) - $2,590,269 (Outside Quarter)
M09111 | T |  | 49779 | M09111 | P-519 - Nova Scotia Power Inc. (NSPI) - (ATO) CI 49779 - L6537 Replacements and Upgrades Phase 2 – $2,331,474
M08783 | T |  | 49782 | M08783 | P-518 - Nova Scotia Power Inc. (NSPI) (ATO) - CI 49782 – L5027B Replacements and Upgrades – $1,655,146
M07981 | D | S | 49787 | M07981 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49787 ‐ Intelligent Feeder Project ‐ $2,782,384
M09154 | T&D |  | 49793 | M09154 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 49793 – L7011 Replacements and Upgrades – $4,810,276 (ATO)
M07655 | G |  | 49804 | M07655 | P-516 - CI #49804 - Nova Scotia Power Inc. (NSPI) WO - HYD Fall River Pipeline Refurbishment - U&U - $275,841
M07655 | G |  | 49804 | M07655 | P-516 - CI #49804 - Nova Scotia Power Inc. (NSPI) WO - HYD Fall River Pipeline Refurbishment - U&U - $275,841
M08364 | O |  | 49855 | M08364 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 49855 - IT Desktop SW Modernization - $4,620,516 - 3rd Quarter 2017
M08395 | O |  | 49857 | M08395 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 49857 - IT Storage Infrastructure - $1,901,189 (Outside Quarter Package)
M09510 | O |  | 49859 | M09510 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI 49859 – IT Windows Server 2008 Upgrade – $1,183,310
M08365 | O |  | 49860 | M08365 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 49860 - IT SharePoint Upgrade - 3,903,594 - 3rd Quarter 2017
M07998 | T&D |  | 49862 | M07998 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49862 – 50N‐410 Trenton Rebuild ‐ $440,329
M07805 |  |  | 49869 | M07805 | P-516 - CI # 49869 - ICP-Armour Stone Replacement - $2,793,935
M09027 | G |  | 49876 | M09027 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 49876 - Real Time Economic Dispatch (P&A)
M07803 | T |  | 49879 | M07803 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI # 49879 - 77V-T52 Replacement - $772,208
M09109 | D |  | 49898 | M09109 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 49898 – 15N-202 Victoria St Replace Deteriorated Assets – $394,528
M07854 | T&D |  | 49922 | M07854 | P-128.17 - Nova Scotia Power (NSPI) - CI 49922 – Western Switching Upgrades (2017) – $378,843
M09155 | T |  | 49922 | M09155 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 49922 – Western Switching Upgrades – $652,142 (ATO)
M08781 | G |  | 49926 | M08781 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 49926 – LM6000 TUC4 Airhouse Upgrade – $987,141
M07971 | T |  | 49928 | M07971 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49928 ‐ 3S Gannon Road – Bus Reconfiguration ‐ $371,395
M08635 | T |  | 49928 | M08635 | P-518 - Nova Scotia Power Inc. (NSPI) - CI# 49928 - 3S Gannon Road Bus Reconfiguration (ATO) - $741,486 (Outside Quarter)
M07972 | T&D |  | 49929 | M07972 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 49929 ‐ Tap Changer Replacements ‐ $318,236
M08782 | G |  | 49940 | M08782 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 49940 – LM6000 TUC5 Control System Upgrade– $1,275,559
M08396 | O |  | 49953 | M08396 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 49953 - IT CIS High Availability - $519,023(Outside Quarter Package)
M08095 | G |  | 50017 | M08095 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 50017 - TUC4 CEMS Installation U&U - $410,817
M08094 | G |  | 50018 | M08094 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 50018 - TUC5 CEMS Installation U&U - $450,496
M08397 | G |  | 50020 | M08397 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 50020 - LIN CEMS Replacement - $633,355 (Outside Quarter Package)
M08366 | O |  | 50113 | M08366 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 50113 - Customer Experience - Streetlight Improvements - $875,836 - 3rd Quarter 2017
M07766 | G |  | 50151 | M07766 | P-516 - CI 50151 - HYD WRC Main Access Entrance Bridge Replacement - $716,508 (Partially Confidential)
M08291 | O |  | 50153 | M08291 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 50153 – Customer Experience Self-Serve Development Phase 2 – $1,160,528 (Filed outside Quarter Package 2017)
M07943 | G |  | 50192 | M07943 | P-517 - Nova Scotia Power Inc. (NSPI) - U&U - CI 50192 – TRE5 Turbine Valve Refurbishment – $391,152
M08367 | O |  | 50292 | M08367 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI# 50292 - Kempt Road and Dartmouth East Depot Truck Bays - $1,095,720 - 3rd Quarter 2017
M08224 | O |  | 50295 | M08224 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 50295 – Electric Vehicle Charging Station Network Pilot Project - $419,908
M08049 | T&D |  | 50341 | M08049 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 50341 ‐ 2017 Substation Recloser Replacements – $604,889
M07997 | T&D |  | 50772 | M07997 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) - CI 50772 – 37N‐412 Rebuild ‐ $771,476
M07994 | D |  | 50796 | M07994 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) -CI 50796 – New Distribution Rights‐of‐Way Phase II ‐ $3,353,445
M07995 | T&D |  | 50800 | M07995 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) - CI 50800 – 1C‐411 Reinsulate ‐ $442,732
M07980 | G |  | 51052 | M07980 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 51052 ‐ TRE6 Generator High Voltage Bushings Critical Spare ‐ $264,250
M08051 | G |  | 51053 | M08051 | P-128.17 - Nova Scotia Power Inc. (NSPI) - CI 51053 ‐ TRE6 HIP Turbine Diaphragm Partition Refurbishment ‐ $1,185,445
M08182 | G |  | 51317 | M08182 | P-517 - Nova Scotia Power Inc. (NSPI) (U&U) - CI 51317 – TRE5 CW Inlet System Refurbishment – $390,035 (2017 filed outside quarter)
M08296 | T |  | 51404 | M08296 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) - CI 51404 – 2017 – 2019 Steel Tower Life Extension – $2,981,318 (Filed outside Quarter Package Sept. 2017)
M08093 | G |  | 51409 | M08093 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 51409 - LIN Track Dozer Replacement U&U - $985,497
M09001 | O |  | 51481 | M09001 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI 51481 – IT ‐ Content Management System Replacement – $2,048,854
M08400 | O |  | 51484 | M08400 | P-128.17 - Nova Scotia Power Inc. (NSPI) - (U&U) CI# 51484 - IT SCADA Network FIrewall - $365,737 (Outside Quarter Package)
M08398 | O |  | 51485 | M08398 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) CI# 51485 - IT Threat Management- $813,449 (Outside Quarter Package)
M08092 | G |  | 51526 | M08092 | P-517 - Nova Scotia Power Inc. (NSPI) - CI 51526 - CT Tusket Generator Replacement - $3,190,415
M08812 | G |  | 51526 | M08812 | P-518 - Nova Scotia Power Inc. (NSPI) - CI 51526 - CT Tusket Generator Replacement - $3,810,417
M08217 | T |  | 51593 | M08217 | P-517 - Nova Scotia Power Inc. (NSPI) (U&U) - CI 51593 – HYD WRC Wicket Gate Thrust Assembly Refurbishment – $667,024
M08181 | G |  | 51711 | M08181 | P-517 - Nova Scotia Power Inc. (NSPI) - (P&A) - CI 51711 – CT Burnside #2 Generator Replacement – $2,876,865 (2017 - filed outside quarter)
M08687 | G |  | 51771 | M08687 | P-518 - Nova Scotia Power Inc. (NSPI) - CI 51771 – HYD WRC Tailrace Road Refurbishment U&U – $321,226
M08734 | G |  | 51775 | M08734 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 51775 – HYD Fixed Ladder & Machine Guard Upgrades – $1,985,179
M08478 | G |  | 51788 | M08478 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 51788 – TRE6 Turbine Diaphragm, Packing and Journals Refurbishment – $1,935,087
M08479 | G |  | 51791 | M08479 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 51791 – TRE6 Generator Stator Partial Re‐wedge and Collector Ring – $779,954
M08480 | G |  | 51793 | M08480 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 51793– TRE6 Valve Refurbishment 2017 – $387,934
M08573 | G |  | 51808 | M08573 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 51808 - TUC HFO Piping Refurbishments - $1,239,933
M09156 | G |  | 51808 | M09156 | P-519 - Nova Scotia Power Inc. (NSPI) - CI 51808 – TUC HFO Piping Refurbishment – $3,460,625 (ATO)
M08481 | G |  | 51870 | M08481 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI 51870– TRE6 HEP and FAC Refurbishment – $419,909
M08369 | D |  | 51956 | M08369 | Nova Scotia Power Inc. (NSPI) - CI# 51956 - P6P Mobile Substation Rewind - U&U - $1,516,121 - 3rd Quarter 2017
M08917 | G |  | 52008 | M08917 | P-518 - Nova Scotia Power Inc. (NSPI) (P&A) - CI 52008 – LM6000 ‐ 191‐253 Hot Section and Engine Refurbishment – $3,041,675
M08680 | T |  | 52107 | M08680 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 52107 – Tufts Cove Unit 6 CW Screen Replacement – $856,984
M08916 | G |  | 52143 | M08916 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 52143 – LM6000 ‐ 191‐332 Hot Section and Engine Refurbishment –$3,227,436
M08681 | G |  | 52239 | M08681 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI 52239 – TUC6 Main and Induction Stop Valve Refurbishment – $335,693
M09394 | G |  | 52292 | M09394 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI 52292 – TUC Heavy Fuel Oil Tank Dyke Refurbishment – $495,317
M08828 | T |  | 52323 | M08828 | P-518 - Nova Scotia Power Inc. (NSPI) (P&A) CI# 52323 - Port Hastings 2C BPS Upgrade - $4,201,330
M08640 | G |  | C0006238 | M08640 | P-518 - Nova Scotia Power Inc. (NSPI) - (P&A) CI# C0006238 - TRE5 Baghouse Filter Replacement U&U - $313,508 (Outside Quarter)
M08639 | G |  | C0005181 | M08639 | P-518 - Nova Scotia Power Inc. (NSPI) - (P&A) CI# C0005181 - LIN1 Bottom Ash Refurbishment - $374,953 (Outside Quarter)
M08531 | G |  | C0001660 | M08531 | P-518 Nova Scotia Power Inc. (NSPI) (U&U) - CI C0001660 – HYD Annapolis Stator Repairs – $308,776
M08482 | G |  | C0002020 | M08482 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI C0002020– TRE6 Boiler Water Wall Panel Replacement U&U – $879,008
M08682 | G |  | C0002103 | M08682 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI C0002103 – HYD WRC Unit 1 Wicket Gate Thrust Assembly Refurbishment –
M08954 | D | N | C0002130 | M08954 | P-128.18 - Nova Scotia Power Inc. (NSPI) - CI C0002130 ‐ ADMS Distribution Fault Location – $443,121
M09477 | O |  | C0002137 | M09477 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0002137 – ECC Map Board Replacement – $2,506,268 (Q3)
M09000 | G |  | C0002241 | M09000 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0002241 – IT – Generation Operations Upgrade – $562,680
M08483 | G |  | C0003238 | M08483 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI C0003238– HYD LEQ Plant Output Cable Replacement – $784,311
M08530 | G |  | C0003739 | M08530 | P-518 Nova Scotia Power Inc. (NSPI) (P&A) - CI C0003739 – POT Turbine Valve Refurbishment – $658,753
M08961 | G |  | C0006618 | M08961 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI C0006618 ‐ Little Brook Wind Turbine Decommissioning – $437,734
M08867 | G |  | C0007500 | M08867 | P-518 Nova Scotia Power Inc. (NSPI) (U&U) - CI C0007500 – LIN3 U&U Bottom Ash Refurbishment – $424,051
M08868 | G |  | C0007718 | M08868 | P-518 Nova Scotia Power Inc. (NSPI) (U&U) - CI C0007718 – LIN3 U&U Burner Front Refurbishment – $345,903
M08918 | G |  | C0008005 | M08918 | P-518 - Nova Scotia Power Inc. (NSPI) (U&U) - CI C0008005 – POT ‐ B Coal Mill Overhaul – $406,011
M08866 | G |  | C0009103 | M08866 | P-518 Nova Scotia Power Inc. (NSPI) (P&A) - CI C0009103 – LIN1 P&A Boiler Refurbishment 2018 – $739,657
M09038 | G |  | C0009166 | M09038 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0009166 – TUC1 Boiler Refurbishment (U&U) – $788,906
M08962 | G |  | C0009621 | M08962 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI C0009621 ‐ HYD Big Falls 6 Exciter Replacement U&U – $485,209
M08829 | T&D |  | C0009898 | M08829 | P-518 -Nova Scotia Power Inc. (NSPI) (P&A) CI# C0009898 - 2C-402 Reinsulate - $861,166
M09609 | O |  | C0010019 | M09609 | P-128-20 Nova Scotia Power Inc. (NSPI) CI C0010019 - IT - ADMS Upgrade - $9,626,891
M09478 | O |  | C0010838 | M09478 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0010838 – MCC - HVAC Replacement – $1,105,002
M08960 | O |  | C0011000 | M08960 | P-518 - Nova Scotia Power Inc. (NSPI) - (P&A) CI C0011000 ‐ IT – Cloud Access Security Broker Infrastructure – $373,647
M09350 | O |  | C0011059 | M09350 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0011059 – IT – Database Infrastructure – $721,816
M09039 | G |  | C0011181 | M09039 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0011181 – HYD LEQ Stator Refurbishment (U&U) – $2,051,177
M09511 | O |  | C0011378 | M09511 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0011378 – Route Network Upgrade – $5,717,752
M09149 | O |  | C0011380 | M09149 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0011380 – 2019 Telecom Building Replacement – $299,657
M09239 | O |  | C0011679 | M09239 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0011679 – AMO T&D Asset Management Performance Tool – $699,974
M08919 | T&D |  | C0011738 | M08919 | P-518 - Nova Scotia Power Inc. (NSPI) (U&U) - CI C0011738 – 1H Firewall Construction – $850,483
M09157 | O |  | C0011858 | M09157 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0011858 – FAC Lower Water Street Roof Replacement – $1,672,596 (U&U)
M09112 | G |  | C0012538 | M09112 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0012538 – HYD Sandy Lake 3 Rotor Refurbishment U&U – $450,381
M08963 | G |  | C0012718 | M08963 | P-518 - Nova Scotia Power Inc. (NSPI) - (U&U) - CI C0012718 ‐ HYD Fourth Lake Turbine Hub Refurbishment U&U – $271,630
M08999 | T&D | N | C0013438 | M08999 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0013438 - IT - T&D WAM Phase 1 - GIS and Field Design - $7,978,434
M09242 | G |  | C0013578 | M09242 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0013578 – TRE Circulating Water Fish Barrier U&U– $1,454,175
M09150 | O |  | C0013718 | M09150 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0013718 – AMO Run‐up Optimization Tool – $406,117
M09208 | G |  | C0013738 | M09208 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0013738 – TUC2 South Boiler Feedwater Pump Refurbishment – $735,544 (U&U)
M09596 | G |  | C0013838 | M09596 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0013838 - Wreck Cove Life Extension and Modernization - $109,214,439
M09113 | G |  | C0014780 | M09113 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0014780 – HYD LEQ Water Passage Refurbishment U&U – $601,188
M09209 | O |  | C0015198 | M09209 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0015198 – 50V Kentville Aluminum Light Pole Replacement – $613,184
M09352 | D |  | C0017084 | M09352 | P-128.19 - Nova Scotia Power Inc. (NSPI) -CI C0017084 – 74N – Springhill Substation Access Road River Crossing – $782,109
M09241 | G |  | C0017920 | M09241 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0017920 – PTMT – Shuttle Belt Replacement– $658,560
M09207 | D |  | C0018059 | M09207 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0018059 – 58C-403 Rebuild Hwy 19 South West Margaree – $1,127,220 (P&A)
M09240 | O |  | C0018485 | M09240 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0018485 – AMO – Wind Asset Management Implementation – $399,796
M09560 | G |  | C0018880 | M09560 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0018880 - VJ2 Engine P686622 Refurbishment - $2,140,601
M09739 |  |  | C0019379 | M09739 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0019379 – 50N-410 – 4C-430 Highway 104 Twinning – $1,137,223
M09479 | O |  | C0020338 | M09479 | P-519 - Nova Scotia Power Inc. (NSPI) (P&A) - CI C0020338 – AMO Meridium Upgrade for Power Production – $1,571,516
M09708 | G |  | C0020385 | M09708 | P-128.20 Nova Scotia Power Inc. (NSPI) - CI C0020385 – LIN Heavy Oil Tank Refurbishment – $3,309,341
M09348 | O |  | C0021006 | M09348 | P-128.19 - Nova Scotia Power Inc. (NSPI) - CI C0021006 – IT – Microsoft Exchange Upgrade – $1,013,478 -ACE amount $1,517,875
M09480 | T |  | C0021105 | M09480 | P-519 - Nova Scotia Power Inc. (NSPI) (P&A) - CI C0021105 – L7002 Replacements and Upgrades Phase 1 – $3,121,442
M09512 | G |  | C0021202 | M09512 | P-519 - Nova Scotia Power Inc. (NSPI) - CI C0021202 – TRE Abercrombie Ash Management Site Water Treatment System Upgrade – $1,039,746
M09709 | O |  | C0021805 | M09709 | P-128.20 Nova Scotia Power Inc. (NSPI) (2020 Q1) - CI C0021805 – IT - Microsoft Enterprise Agreement 2020 – $3,139,727
M09659 | T |  | C0023622 | M09659 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0023622 – AMO Substation and Transmission Asset Performance Management Program – $2,217,589
M09660 | D |  | C0023623 | M09660 | P-128.20 - Nova Scotia Power Inc. (NSPI) - CI C0023623 – AMO Distribution Asset Performance Management Program – $1,721,484
M09710 | D |  | C0024486 | M09710 | P-520 Nova Scotia Power Inc. (NSPI) (2020 Q1) - CI C0024486 – 2S-T1 Transformer Replacement – $2,648,403 (U&U)
M05583 | O |  | General | M05583 | P-128.13 - NSPI WO - CI General Plant Routines (2012) - Outside Quarter March 13, 2013 - $884,238
M05584 | D |  | Routine | M05584 | P-128.13 - NSPI WO - CI Distribution Routines (2012) - Outside Quarter March 13, 2013 - $26,624,197
M06695 | T |  | Routine | M06695 | CI Variuos - P-128.14 - NSPI WO - ATO - Transmissions Routines - $5,352,171. ACE amount $4,677,539. ATO amount $674,633
M06696 | D |  | Routine | M06696 | CI Various - P-128.14 - NSPI WO - ATO - Distribution Routines - $23,536,221. ACE amount $22,334,401. ATO amount $1,201,821
M06976 | T |  | Routine | M06976 | CI Various - P-128.14 - NSPI WO - ATO - Transmissions Routines - Revised - $4,825,054. ACE amount $4,677,539. ATO amount $147,515
M06977 | D |  | Routine | M06977 | CI Various - P-128.14 - NSPI WO - ATO - Distribution Routines - $2,645,434. ACE amount $2,476,304. ATO amount $169,130
M07456 | D |  | Routine | M07456 | P-515 - CI Various - Nova Scotia Power Inc. (NSPI) - ATO: Distribution Routines: D004 - New Customer Upgrades: ATO amount $498,272;D005 - Unplanned Replace Deteriorated: ATO amount $265,658; D051 - System Performance Improvement Routine: ATO amount $517,190; D061 - New Customers - Residential: ATO amount $438,902; D062 - New Customers - Commercial: ATO amount $1,673,375
M07458 | T |  | Routine | M07458 | P-515 - CI Various - Nova Scotia Power Inc. (NSPI) - ATO: Transmission Routines:
M07923 | D |  | Routine | M07923 | P-516 - Nova Scotia Power (NSPI) - 2016 Ace Plan - Routine Capital - ATO - Distribution Routines:
M07926 | T |  | Routine | M07926 | P-516 - Nova Scotia Power Inc. (NSPI) - 2016 Ace Plan - Routine Capital - ATO - Transmission Routines:
M08683 | D |  | Routine | M08683 | P-518 - Nova Scotia Power Inc. (NSPI) - Distribution Routines ATO - CI Various (D005, D008, D051, D061)
M08685 | T |  | Routine | M08685 | P-518 - Nova Scotia Power Inc. (NSPI) - Transmission Routines ATO - CI Various (T001, T003)
M09146 | D |  | Routine | M09146 | P-519 - Nova Scotia Power Inc. (NSPI) - (ATO) - Distribution Routines – Non‐Confidential
M09148 | T |  | Routine | M09148 | P-519 - Nova Scotia Power Inc. (NSPI) - Transmission Routines – Non‐Confidential
M09656 | D |  | Routine | M09656 | P-520 - Nova Scotia Power Inc. (NSPI) - Distribution Routines (ATO) - $31,920,113
M09658 | T |  | Routine | M09658 | P-519 - Nova Scotia Power Inc. (NSPI) - T001 – Provincial Transmission Line Replacements - Unplanned: ATO amount $2,091,266
M04941 | T |  | Various | M04941 | CI# Various - P-128.12 - NSPI WO - Transmission Routines (2011) - $264,292
M05068 | D |  | Various | M05068 | CI# Various - P-128.12 - NSPI WO - Distribution Upgrades and Replacement Routines (2011)
M04942 | O |  | Various | M04942 | CI# Various - P-128.12 - NSPI WO - General Property Routines (2011) - $264,292
M04943 | G |  | Various | M04943 | CI# Various - P-128.12 - NSPI WO - Generation Hydro Routine (2011) - $528,179
M07675 | XXX |  | Various | M07675 | P-141 - Nova Scotia Power Inc. - Request Approval of 2017 Wholesale Market Back-up/Top-up (BUTU) Service Applications by Municipal Customers
M07745 | ACE |  | Various | M07745 | P-128.17 - Nova Scotia Power Inc. - 2017 ACE Plan Application for approval of $152.8 million of its Annual Capital Expenditure ("ACE Plan") which totals $398 million
M07924 | O |  | Routine | M07924 | P-516 - Nova Scotia Power Inc. (NSPI) - 2016 Ace Plan - Routine Capital - ATO - General Plant Routines:
M07938 | G |  | 47947 | M07938 | P-128.16 - Nova Scotia Power Inc. (NSPI) - 2016 Ace Plan CI Less than $250 Thousand - CI 47947 – TUC6 Condenser Waterbox Coating Replacement – $366,978
M08030 | MUNI |  | Various | M08030 | E-BER-E-17 Town of Berwick on behalf of the Berwick Electric Commission - Capital Expenditure - purchase of a new hot line aerial bucket truck
M08178 | G |  | Routine | M08178 | P-128.17 - Ace Plan Routines - Nova Scotia Power Inc. (NSPI) - S001 Routine ‐ PHB ‐ Routine Equipment Replacements ‐ $170,000;
M08350 | ACE |  | Various | M08350 | P-128.18 - Nova Scotia Power Inc. (NSPI) - 2018 Ace Plan - $354.9 million
M08523 | G |  | Various | M08523 | P-128.05 - Approval of Air Emissions Strategy Capital Projects
M08548 | MUNI |  | Various | M08548 | E-BER-E-18 -Town of Berwick on behalf of the Berwick Electric Commission - Refurbishment of Control Structure, re-enforcement of DAM, etc.
M08684 | O |  | Routine | M08684 | P-518 - Nova Scotia Power Inc. (NSPI) - General Plant Routines - P062 – Work Vehicle Replacements: ATO amount $486,872
M08984 | ACE |  | Various | M08984 | P-128.19 - Nova Scotia Power Inc. - 2019 ACE Plan Application - Requesting approval of $190.4 million of its 2019 ACE Plan which totals $333.2 million
M09147 | O |  | Routine | M09147 | P-519 - Nova Scotia Power Inc. (NSPI) - General Plant Routines – Non‐Confidential
M09327 | G |  | Various | M09327 | P-531 - NSPC Application for 150 MW CFB Coal-Fired Thermal Plant, Point Aconi, Cape Breton County (1989)
M09499 | ACE |  | Various | M09499 | P-128.20 - Nova Scotia Power Inc. - 2020 ACE Plan Application
M09657 | O |  | Routine | M09657 | P-519 - Nova Scotia Power Inc. (NSPI) - General Plant Routines - P062 – Work Vehicle Replacements: ATO amount $651,546
M09674 | MUNI |  | Various | M09674 | E-BER-E-20 -Town of Berwick on behalf of the Berwick Electric Commission - Substation Transformer Project - $471,777
M09683 | G |  | Various | M09683 | E-BER-E-20 Town of Berwick on behalf of the Berwick Electric Commission - Burnt Dam Project
M05339 | ACE |  | Various | M05339 | P-128.13 - Nova Scotia Power Inc. - 2013 Annual Capital Expenditure Plan ("ACE Plan")
M05355 | ACE |  | Various | M05355 | P-205 Capital Expenditure Justification Criteria CEJC - Nova Scotia Power Inc.
M05360 | XXX |  | Various | M05360 | P-141 - Nova Scotia Power Inc. - Request Approval of the 2013 Annually Adjusted Rates (AAR's)
M05733 | MUNI |  | Various | M05733 | E-BER-R-13(2) - Berwick Electric Commission - Request interim approval under s69 of the Public Utilities Act to offer LED Yard Lighting to customers
M05960 | XXX |  | Various | M05960 | P-141 - Nova Scotia Power Inc. - Request Approval of the 2014 Annually Adjusted Rates (AAR's)
M05998 | ACE |  | Various | M05998 | P-128.14 - Nova Scotia Power Inc. - 2014 ACE Plan requesting approval of capital investments totaling $97.1 million
M06083 | G |  | Various | M06083 | P-207 - Nova Scotia Power Inc. - Sable Wind Project
M06293 | MUNI |  | Various | M06293 | E-ANT-E-14 - Antigonish Electric Utility - Purchase of New Utility Bucket Truck - $284,45506292
M06499 | MUNI |  | Various | M06499 | E-LUN-R-14(3)- Lunenburg Electric Utility - Request approval of Capital Expenditure and Board Opinion - 2014/15 Capital Budget
M06508 | ACE |  | Various | M06508 | P-128.14 - Nova Scotia Power Inc. - 2014 ACE Directive 5 Report - Capital Planning & Capital Expenditure Justification Criteria - November 4, 2014
M06514 | ACE |  | Various | M06514 | P-128.15 - Nova Scotia Power Inc. - 2015 ACE Plan Application for approval of $138.7 million of its Annual Capital Expenditure ("ACE Plan") which totals $273.0 million.
M06517 | XXX |  | Various | M06517 | P-141 - Nova Scotia Power Inc. - Request Approval of the 2015 Annually Adjusted Rates (AAR's)
M07086 | MUNI |  | Various | M07086 | E-ANT-E-15 - Town of Antigonish Electric Utility - Wind Energy Project - Capital Expenditure Request
M07169 | XXX |  | Various | M07169 | P-141 - Nova Scotia Power Inc. - Request Approval of the 2016 Annually Adjusted Rates (AAR's)
M07176 | ACE |  | Various | M07176 | P-128.16 - Nova Scotia Power Inc. (NSPI) 2016 ACE Plan Application for approval of $174.4 million of its Annual Capital Expenditure ("ACE Plan") which totals $279.9 million.
M07457 | O |  | Various | M07457 | P-515 - CI Various - Nova Scotia Power Inc. (NSPI) ATO: General Plant Routines:
M07675 | XXX |  | Various | M07675 | P-141 - Nova Scotia Power Inc. - Request Approval of 2017 Wholesale Market Back-up/Top-up (BUTU) Service Applications by Municipal Customers
M07745 | ACE |  | Various | M07745 | P-128.17 - Nova Scotia Power Inc. - 2017 ACE Plan Application for approval of $152.8 million of its Annual Capital Expenditure ("ACE Plan") which totals $398 million

## Snapshot Summary
System Snapshot Summary of Transformer Capacity Data
| Year | Constrained System (MVA) | [5 empty] | Constrained MVA + |  | Total Xfmr Peak MVA *
|  | Halifax | Canseau | Northern | Sydney | Valley | Western | Per Year | 4-Yr Max | Per Year | 4-Yr Max
| 2017 | 315.69 | 0 | 95.71 | 0 | 69.67 | 35.68 | 516.75 | 661.3261 | 1679.716 | 1863.2132
| 2018 | 349.208 | 0 | 49.5241 | 0 | 127.002 | 43.5345 | 569.2685 |  | 1863.2132
| 2019 | 265.7923 | 0 | 32.4176 | 0 | 131.6106 | 84.7975 | 514.618 |  | 1798.1601
| 2020 | 230.6981 | 0 | 46.275 | 0 | 128.1568 | 19.7165 | 424.8464 |  | 1694.188 |  | Equivilant growth rate taken from 2011-2020 Projects Tab
[6 empty] | Growth | 1.075% | MVA | 7.1093 |  |  | Constrained growth = Constrained MVA x Growth Rate
| Notes: | This table provides a summary of results determined from the Region spreadsheet tabs (Halifax, Canseau,…)
+ Constrained MVA includes distribution load and losses but does not include transmission connected load or losses (i.e., based on substation transformer & feeder metering)
* Total Peak MVA includes distribution load and losses but does not include transmission connected load or losses
The Constrained designation is applied to infrastructure operating at ≥ 80% of Capital Expenditure Justification Criteria capacity, as follows:
1 | Constrained transformer = unit loaded ≥ 80% of 133% CEJC Criteria limit = 106%
2 | Constrained Feeders = average substation feeder load ≥ 80% x 325 amps = 260 amps
3 | Constrained Radial Transmission Line = peak load ≥ 80% of (lesser of 60MW Looping Policy and winter line rating)
4 | If loading exceeds any of these values during any of the previous 4 years (chosen because we have 4 years of snapshot data), then the equipment is considered to be constrained.
| Growth | 1.075%
| Year | Radial Xmsn | Xfmr % | Feeder (A)
| 0 | 80% | 106% | 260
| 1 | 80.86% | 107.1% | 262.795
| 2 | 81.73% | 108.3% | 265.62
| 3 | 82.61% | 109.5% | 268.4755
| 4 | 83.5% | 110.6% | 271.3616
| 5 | 84.39% | 111.8% | 274.2787
| 6 | 85.3% | 113% | 277.2272
| 7 | 86.22% | 114.2% | 280.2074
| 8 | 87.14% | 115.5% | 283.2196
| 9 | 88.08% | 116.7% | 286.2642
| 10 | 89.03% | 118% | 289.3416
| 11 | 89.99% | 119.2% | 292.452
| 12 | 90.95% | 120.5% | 295.5959
| 13 | 91.93% | 121.8% | 298.7735
| 14 | 92.92% | 123.1% | 301.9853
| 15 | 93.92% | 124.4% | 305.2317
| 16 | 94.93% | 125.8% | 308.5129
| 17 | 95.95% | 127.1% | 311.8294
| 18 | 96.98% | 128.5% | 315.1816
| 19 | 98.02% | 129.9% | 318.5698
| 20 | 99.08% | 131.3% | 321.9944
| 21 | 100.1% | 132.7% | 325.4559
| 22 | 101.2% | 134.1% | 328.9545
| 23 | 102.3% | 135.6% | 332.4908
| 24 | 103.4% | 137% | 336.065
| 25 | 104.5% | 138.5% | 339.6777

## Halifax
HALIFAX OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: -13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  |  | Subs | xfmrs | Feeders
1 | 1H | WATER STREET | 138 | T61 | 40/53 | 26.4 | 20.89 | 16.1447 | 13.4373 | 15.397 | 53 | 39.42% | 3 | 6.9633 | 152.2834 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 795 |  | 2 |  |  | 608 | - |  | 1 | 1 | 3
2 | 1H | WATER STREET | 138 | T62 | 40/53 | 26.4 | 14.65 | 15.1855 | 19.5339 | 26.1168 | 53 | 49.28% | 3 | 8.7056 | 190.3857 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1 | 3
| 1H | WATER STREET | 138 | T63 | 40/53 | 26.4 | 28.98 | 39.2689 | 29.7501 | 30.1412 | 53 | 74.09% | 3 | 13.0896 | 286.2618 | 28.98 | 39.2689 | 29.7501 | 30.1412 | 39.2689 |  | y | y | [9 empty] | 1 | 1 | 3
#REF! | 2H | ARMDALE | 138 | T61 | 25/32/42 | 26.4 | 31.93 | 28.1599 | 31.4647 | 33.8585 | 42 | 80.62% | 3 | 11.2862 | 246.8208 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 795 |  | 2 |  |  | 608 | - |  | 1 | 1 | 3
| 2H | ARMDALE | 138 | T62 | 25/32/42 | 26.4 | - | - | - | - | 42 | 0% | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | y | y | [9 empty] | 1 | 1 | 4
#REF! | 20H | SPRYFIELD | 69 | T1 | 15/20//22.4 | 13.2 | 36.3 | 40.3736 | 36.4085 | 32.0045 | 50.4 | 80.11% | 6 | 6.7289 | 294.3147 | 36.3 | 40.3736 | 36.4085 | 32.0045 | 40.3736 | y | y | y | R | 336 | 1 |  |  |  | 60 | 67.29% |  | 1 | 1 | 6
#REF! | 20H | SPRYFIELD | 69 | T2 | 15/20/25//28 | 13.2 | [15 empty] | y | y | [9 empty] | 1 | 1
#REF! | 23H | ROCKINGHAM | 69 | T51 | 15/20/25 | 13.2 | 20.47 | 21.32 | 22.6794 | 24.4729 | 25 | 97.89% | 4 | 6.1182 | 267.6028 | 20.47 | 21.32 | 22.6794 | 24.4729 | 24.4729 | n | y | y | R | 4/0 |  | 1 |  |  | 45 | 54.38% |  | 0 | 1 | 4
#REF! | 40H | WOODLAWN | 69 | T51 | 7.5/10/12.5 | 26.4 | 4.53 | 5.05 | 4.7922 | 4.0775 | 12.5 | 40.4% | 1 | 5.05 | 110.4401 | 0 | 0 | 0 | 0 | 0 | y | n | y | N | 636 | 2 |  |  |  | 260 | - |  | 1 | 0 | 1
| 40H | WOODLAWN | 69 | T52 | 15/20//22.4 | 13.2 | 15.46 | 14.55 | 14.1114 | 13.5353 | 22.4 | 69.02% | 4 | 3.865 | 169.0499 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1 | 4
#REF! | 48H | PENHORN | 69 | T1 | 15/20//22.4 | 12.47 | 15.26 | 18.095 | 19.6538 | 19.388 | 22.4 | 87.74% | 4 | 4.9135 | 227.4885 | 0 | 0 | 0 | 0 | 0 | y | n | y | N | 556 | 2 |  |  |  | 202 | - |  | 1 | 0 | 4
#REF! | 54H | MAPLE STREET | 69 | T3 | 15/20/25//28 | 13.2 | 15.44 | 14.8077 | 13.771 | 13.5977 | 28 | 55.14% | 4 | 3.86 | 168.8312 | 0 | 0 | 0 | 0 | 0 | y | y | y | R | 556 | 2 |  |  |  | 240 | - |  | 1 | 1 | 4
#REF! | 58H | IMPERIAL OIL DIST | 69 | T3 | 15/20/25 | 26.4 | - | 17.1829 | 17.0859 | 15.5898 | 25 | 68.73% | 2 | 8.5914 | 187.8887 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556/636 | 2 |  |  |  | 222 | - |  | 1 | 1 | 2
#REF! | 62H | ALBRO LAKE ROAD | 69 | T1 | 15/20//22.4 | 12.47 | 7.56 | 11.8403 | 9.6325 | 10.6483 | 22.4 | 52.86% | 4 | 2.9601 | 137.0487 | 0 | 0 | 0 | 0 | 0 | y | n | y | R | 556 |  | 1 |  |  | 82 | 19.73% |  | 1 | 0 | 4
#REF! | 87H | MUSQUODOBOIT HBR. | 138 | T61 | 15/20/25 | 13.2 | 14.18 | 11.6716 | 11.2789 | 15.2753 | 25 | 61.1% | 3 | 5.0918 | 222.7065 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 556 |  | 1 |  |  | 201 | 25.46% |  | 0 | 0 | 0
#REF! | 88H | UP MUSQUODOBOIT | 69 | T51 | 15/20/23//26 | 25 | 7.58 | 8.8641 | 12.1785 | 16.0444 | 26 | 61.71% | 2 | 8.0222 | 185.2649 | 0 | 0 | 0 | 0 | 0 | y | y | y | R | 2/0 | 1 |  |  |  | 34 | 47.19% |  | 1 | 1 | 2
#REF! | 92H | TIDEWATER | 138 | T61 | 7.5/10/12.5 | 13.2 | 15.05 | 13.8389 | 12.8008 | 10.4552 | 12.5 | 120.4% | 3 | 5.0167 | 219.4223 | 15.05 | 13.8389 | 0 | 0 | 15.05 | n | n | n | R | 556 |  | 1 |  |  | 165 | 25.08% |  | 0 | 0 | 0
#REF! | 96H | RUTH FALLS HYDRO | 69 | T53 | 7.5/10//11.2 | 25 | 5.61 | 6.2003 | 5.078 | 5.1789 | 11.2 | 55.36% | 2 | 3.1001 | 71.5943 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 1/0 | 1 |  |  |  | 29 | 21.38% |  | 0 | 0 | 0
#REF! | 99H | FARRELL STREET | 69 | T51 | 15/20/25 | 13.2 | 12.06 | 6.1181 | 11.1523 | 10.1958 | 25 | 48.24% | 2 | 6.03 | 263.7441 | 12.06 | 6.1181 | 11.1523 | 10.1958 | 12.06 | y | y | n | N | 556/795 | 5 |  |  |  | 284 | - |  | 1 | 1 | 0
#REF! | 101H | COBEQUID ROAD | 138 | T61 | 25/33.3/42//46.7 | 26.4 | 28.16 | 29.53 | 27.3716 | 25.5935 | 46.7 | 63.23% | 3 | 9.8433 | 215.2671 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 |  | 3 |  |  | 685 | - |  | 1 | 1 | 3
#REF! | 101H | COBEQUID ROAD | 138 | T62 | 28/37.3/47 | 26.4 | 38.91 | 32.83 | 34.8607 | 31.4046 | 47 | 82.79% | 3 | 12.97 | 283.6452 | 38.91 | 32.83 | 34.8607 | 31.4046 | 38.91 |  | y | y | [9 empty] | 1 | 1 | 3
#REF! | 103H | LAKESIDE | 138 | T61 | 25/33.3/41.6//46.6 | 26.4 | 45.54 | 43.7411 | 39.0367 | 38.1432 | 46.6 | 97.73% | 4 | 11.385 | 248.9823 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | MISC |  | 5 |  | 1 | 1626 | - |  | 1 | 1 | 4
28 | 104H | KEMPT ROAD | 138 | T61 | 25/33.3/41.7 | 26.4 | 25.11 | 40.09 | 37.7147 | 20.7187 | 41.7 | 96.14% | 3 | 13.3633 | 292.2471 | 25.11 | 40.09 | 37.7147 | 20.7187 | 40.09 | y | y | y | N | 795 |  | 2 |  |  | 608 | - |  | 1 | 1 | 3
29 | 104H | KEMPT ROAD | 138 | T62 | 25/33.3/41.6//46.7 | 26.4 | 17.83 | 36.35 | 38.3485 | 35.8952 | 46.7 | 82.12% | 4 | 9.5871 | 209.6637 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1 | 4
30 | 104H | KEMPT ROAD | 138 | T63 | 25/33.3/41.6//46.7 | 26.4 | 46.03 | 29.75 | 35.2355 | 45.4517 | 46.7 | 98.57% | 4 | 11.5075 | 251.6613 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1 | 4
#REF! | 108H | BURNSIDE SUB. | 138 | T61 | 25/33.3/41.5 | 26.4 | 25.87 | 18.6232 | 23.0556 | 23.498 | 41.5 | 62.34% | 4 | 6.4675 | 141.4399 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556/795 |  | 3 |  |  | 747 | - |  | 1 | 1 | 4
| 113H | DARTMOUTH EAST | 138 | T63 | 25/33.3/41.5 | 26.4 | 45.73 | 44.57 | 41.9973 | 35.4409 | 41.5 | 110.2% | 4 | 11.4325 | 250.0211 | 45.73 | 44.57 | 0 | 0 | 45.73 | y | y | y | N | 795 |  | 2 |  |  | 402 | - |  | 1 | 1 | 4
#REF! | 113H | DARTMOUTH EAST | 138 | T64 | 25/33/42 | 26.4 | 40.07 | 36.74 | 33.5676 | 17.8342 | 42 | 95.4% | 4 | 10.0175 | 219.076 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1 | 4
#REF! | 124H | AKERLEY BLVD. | 69 | T1 | 7.5/10//11.2 | 12.48 | 8.45 | 10.5647 | 7.7496 | 7.146 | 11.2 | 94.33% | 2 | 5.2824 | 244.3732 | 0 | 0 | 0 | 0 | 0 | y | n | n | N | 556 | 2 |  |  |  | 82 | - |  | 1 | 0 | 0
#REF! | 126H | PORTER'S LAKE | 138 | T61 | 15/20/25 | 13.2 | - | 18.3098 | 14.737 | 6.7685 | 25 | 73.24% | 3 | 6.1033 | 266.9482 | - | 18.3098 | 14.737 | 6.7685 | 18.3098 | y | y | y | R | 556 |  | 1 |  |  | 201 | 45.29% |  | 1 | 1 | 3
#REF! | 127H | AEROTECH PARK | 138 | T61 | 15/20/25 | 26.4 | 14.61 | 19.9928 | 21.3339 | 18.5533 | 25 | 85.34% | 3 | 7.1113 | 155.5197 | 0 | 0 | 0 | 0 | 0 | y | y | y | R | 795 |  | 1 |  |  | 251 | 35.56% |  | 1 | 1 | 3
#REF! | 129H | KEARNEY LAKE RD. | 138 | T61 | 25/33.3/41.5 | 26.4 | 39.64 | 39.4787 | 27.829 | 25.7946 | 41.5 | 95.52% | 3 | 13.2133 | 288.9667 | 39.64 | 39.4787 | 27.829 | 25.7946 | 39.64 | y | y | y | R | 795 |  | 1 |  |  | 251 | 66.07% |  | 1 | 1 | 3
#REF! | 131H | LUCASVILLE ROAD | 138 | T62 | 25/33.3/41.5 | 26.4 | 22.65 | 24.59 | 22.5663 | 21.1545 | 41.5 | 59.25% | 2 | 12.295 | 268.8834 | 22.65 | 24.59 | 22.5663 | 21.1545 | 24.59 | y | y | y | N | 795 |  | 2 |  |  | 184 | - |  | 1 | 1 | 2
| 131H | LUCASVILLE ROAD | 138 | T63 | 25/33/42//46.7 | 26.4 | 30.79 | 28.42 | 28.0944 | 28.0428 | 46.7 | 65.93% | 2 | 15.395 | 336.6783 | 30.79 | 28.42 | 28.0944 | 28.0428 | 30.79 |  | y | y | [9 empty] | 1 | 1 | 2
| 137H | HAMMONDS PLAINS | 138 | T61 | 25/33/42.0 | 26.4 | 27.91 | 23.1069 | 30.2086 | 32.0493 | 42 | 76.31% | 4 | 8.0123 | 175.2239 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 795/1113 |  | 2 |  |  | 301 | - |  | 1 | 1 | 4
| 139H | DARTMOUTH CROSSING | 138 | T61 | //25/33/42.0 | 26.4 | 35.91 | 25.3968 | 30.0646 | 26.5162 | 42 | 85.5% | 4 | 8.9775 | 196.3319 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556/795 |  | 2 |  |  | 402 | - |  | 1 | 1 | 4
[6 empty] | Totals | 759.16 | 790.7554 | 778.5808 | 735.9824 | 1226.1 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 315.69 | 349.208 | 265.7923 | 230.6981 | 369.2852 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [8 empty] | 32 | 29 | 101
|  | Notes: | [21 empty] | Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW. | [7 empty] | Total | 68 | 68 | 189
|  | 48H-T1 to be replaced in 2020 | [6 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year | [15 empty] | Count | 132 | 154 | 413
|  | New Mount Hope transformer to be installed in 2021 | [6 empty] | 2H-T62 | 46.7 | 1272.8 | Added 46.7MVA of transformer capacity at 2H |  |  |  | 2018 | [15 empty] | % | 51.52% | 44.16% | 45.76%

## Canseau
CANSEAU OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: - 13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  | Subs | xfms | Feeders
1 | 1C | PT. TUPPER GS/SUB | 138 | T61 | 15/20/25 | 26.4 | 30.63 | 21.1 | 11.6177 | 5.4206 | 25 | 21.68% | 2 | 2.7103 | 59.2725 | 0 | 0 | 0 | 0 | 0 | y | y | n | N | 556/795 |  | 2 |  |  | 546 | - | 1 | 1 | 0 | Incorrect values not counted - These are adding in wind farm gen as circuit load, when actual peak load on distribution circuits is ~14MVA (the 22MW gen facility would offset this amount, not add to it).
2 | 2C | PORT HASTINGS | 138 | T61 | //15/20/25 | 26.4 | 8.83 | 1.6137 | 2.9069 | 2.3959 | 25 | 35.32% | 2 | 4.415 | 96.5531 | 0 | 0 | 0 | 0 | 0 | y | y | n | N | 556/795 |  | 5 |  |  | 1060 | - | 1 | 1 | 0
#REF! | 4C | LOCHABER ROAD | 138 | T63 | 25/33.3//41.7 | 26.4 | 40.7 | 40.8961 | 36.9802 | 36.4893 | 41.7 | 98.07% | 5 | 8.1792 | 178.8739 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 |  | 2 |  |  | 330 | - | 1 | 1 | 5
#REF! | 9C | ABERDEEN | 69 | T1 | 3//3.36 | 12.47 | - | 0.88474 | 0.73633 | 0.77504 | 4.36 | 20.29% | 1 | 0.88474 | 40.9627 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 1.966% | 0 | 0 | 0
#REF! | 9C | ABERDEEN | 69 | T2 | 1 | 12 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0
#REF! | 19C | CANSO TOWN | 69 | T51 | 3/4//4.48 | 4.16 | 1.28 | 1.7596 | 1.6243 | 1.4407 | 4.48 | 39.28% | 2 | 0.8798 | 122.1043 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 5.175% | 0 | 0 | 0
#REF! | 22C | CLEVELAND | 138 | T61 | 15/20/25.0 | 26.4 | 4.37 | 20.9338 | 8.649 | 6.8288 | 25 | 83.74% | 4 | 5.2334 | 114.452 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 2/0 |  | 1 |  |  | 34 | 61.57% | 0 | 0 | 0
#REF! | 24C | DICKIE BROOK | 69 | T54 | 5.6/6.7//7.55 | 25 | 4.42 | 5.9583 | 6.0099 | 4.8982 | 7.55 | 79.6% | 2 | 3.0049 | 69.3962 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 22.85% | 0 | 0 | 0
#REF! | 57C | SALMON RIVER LAKE | 69 | T1 | 7.5/10/12 | 26.4 | 9.84 | 6.7355 | 5.3602 | 4.5381 | 12 | 82% | 3 | 3.28 | 71.7314 | 0 | 0 | 0 | 0 | 0 | y | y | n | R | 4/0 | 1 |  |  |  | 45 | 39.13% | 1 | 1 | 0
#REF! | 58C | S.W. MARGAREE | 69 | T51 | 7.5/10/12.5//14 | 24.94 | 7.04 | 10.6169 | 6.1115 | 6.2778 | 14 | 75.83% | 2 | 5.3084 | 122.888 | 0 | 0 | 0 | 0 | 0 | y | n | n | R | 336 | 1 |  |  |  | 67 | 29.19% | 1 | 0 | 0
#REF! | 59C | ST. PETER'S | 138 | T61 | 7.5/10/12.5 | 26.4 | 9.73 | 4.7251 | 7.4655 | 10.2432 | 12.5 | 81.95% | 3 | 3.4144 | 74.6706 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 |  | 1 |  |  | 165 | 17.07% | 0 | 0 | 0
#REF! | 67C | WHYCOCOMAGH | 138 | T64 | 15/20/25 | 26.4 | 8.76 | 9.3784 | 6.6269 | 7.9054 | 25 | 37.51% | 2 | 4.6892 | 102.5494 | 0 | 0 | 0 | 0 | 0 | y | n | n | R | 556/636 |  | 1 |  |  | 45 | 20.84% | 1 | 0 | 0
#REF! | 100C | CAPE PORCUPINE | 138 | T61 | 8.4/11.2/14 | 26.4 | 2.95 | 5.2708 | 3.4064 | 6.2317 | 14 | 44.51% | 3 | 2.0772 | 45.4279 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 556 |  | 2 |  |  | 330 | - | 0 | 0 | 0
#REF! | 103C | CHETICAMP | 69 | T51 | 7.5/10/12.5 | 13.2 | 6.9 | 4.4237 | 6.7006 | 5.1928 | 12.5 | 55.2% | 3 | 2.3 | 100.5989 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 67 | 11.5% | 0 | 0 | 0
[6 empty] | Totals | 135.45 | 134.2965 | 104.1954 | 98.6375 | 223.09 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [7 empty] | 6 | 4 | 5
Notes:
|  | Weather taken from Halifax Int A Station Gov. of Canada Website | [21 empty] | Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW.
[9 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year

## Northern
NORTHERN OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: - 13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  |  | xfms | Feeders
1 | 1N | ONSLOW | 138 | T1 | 9/12/15//16.8 | 26 | 5.27 | 4.15 | 4.0835 | 4.0828 | 16.8 | 31.37% | 1 | 5.27 | 117.0245 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556/795/ 1113 |  | 4 |  |  | 1186 | - | 1 | 1 | 1
2 | 1N | ONSLOW | 138 | T4 | 9/12/15//16.8 | 26 | 10.1 | 9.73 | 10.0686 | 9.939 | 16.8 | 60.12% | 1 | 10.1 | 224.2784 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1
3 | 1N | ONSLOW | 138 | T65 | 25/33.3/41.7 | 26 | 18.59 | 15.51 | 18.1827 | 19.9612 | 41.7 | 47.87% | 3 | 6.6537 | 147.751 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 3
3 | 3N | OXFORD JUNCTION | 69 | T51 | 13.5/20.0 | 26.4 | 7.9 | 3.0051 | 3.9662 | 6.0064 | 20 | 39.5% | 2 | 3.95 | 86.3838 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 556 | 1 |  |  |  | 82 | 29.49% | 0 | 0 | 0
4 | 4N | TATAMAGOUCHE | 69 | T51 | 7.5/10/12.5 | 13.2 | - | 9.9183 | 9.378 | 8.0408 | 12.5 | 79.35% | 3 | 3.3061 | 144.6038 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 60 | 16.53% | 0 | 0 | 0
5 | 6N | BLACK RIVER ROAD | 69 | T1 | 5//5.6 | 12.47 | 8.31 | 5.6078 | 5.5662 | 5.2179 | 5.6 | 100.1% | 2 | 4.155 | 192.3729 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 18.47% | 0 | 0 | 0 | Incorrect value not counted: Likely cold load pick-up
6 | 7N | PUGWASH | 69 | T3 | 2 | 12.47 | 1.22 | 1.2153 | 1.289 | 1.1679 | 2 | 64.45% | 1 | 1.289 | 59.6807 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 556 | 1 |  |  |  | 82 | 16.32% | 0 | 0 | 0
7 | 7N | PUGWASH | 69 | T54 | 5//5.6 | 12.47 | 4.25 | 4.2499 | 4.462 | 4.0877 | 5.6 | 79.68% | 1 | 4.462 | 206.587 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
| 7N | PUGWASH | 69 | T1 | 3/4//4.48 | 4.16 | 1.85 | 1.8472 | 1.77 | 1.71 | 4.48 | 41.29% | 1 | 1.85 | 256.7543 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
| 7N | PUGWASH | 69 | T55 | 3/3.75 | 4.16 | 1.96 | 1.9623 | 1.95 | 2.19 | 3.75 | 58.4% | 5 | 0.438 | 60.7883 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
#REF! | 15N | WILLOW LANE | 69 | T1 | 7.5/10.0 | 4 | 10.46 | 2.5794 | 2.7176 | 2.4573 | 10 | 27.18% | 2 | 1.3588 | 196.1223 | 0 | 0 | 0 | 0 | 0 | y | y | n | R | 336 | 1 |  |  |  | 60 | 55.18% | 1 | 1 | 0 | Incorrect value not counted: 4kV being converted to 25kV
#REF! | 15N | WILLOW LANE | 69 | T2 | 15/20/25.0 | 26.4 | 25.56 | 26.4988 | 18.3216 | 23.6594 | 25 | 106% | 2 | 13.2494 | 289.755 | 25.56 | 26.4988 | 18.3216 | 23.6594 | 26.4988 |  | y | n | [9 empty] | 1 | 0
#REF! | 15N* | WILLOW LANE | 69 | T3 | 15/20/25//28.0 | 26.4 | 17.78 | 9.9508 | 6.7285 | 0 | 18 | 98.78% | 2 | 8.89 | 194.4183 | 0 | 0 | 0 | 0 | 0 |  | y | n | [9 empty] | 1 | 0
#REF! | 16N | STEWIACKE | 69 | T1 | 7.5/10/11.2 | 12.48 | 9.03 | 9 | 8.7868 | 11.1842 | 11.2 | 99.86% | 2 | 5.5921 | 258.7012 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 60 | 18.64% | 0 | 0 | 0
#REF! | 17N | BROWNELL AVENUE | 69 | T1 | 5 | 4.16 | 2.97 | 1.0761 | 4.2417 | 2.7 | 5 | 84.83% | 4 | 1.0604 | 147.1713 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 24.83% | 0 | 0 | 0
#REF! | 20N | PARK STREET | 69 | T1 | 5 | 3.98 | 1.68 | 0.86683 | 3.6761 | 4.2 | 5 | 84% | 3 | 1.4 | 203.088 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 12.35% | 0 | 0 | 0
#REF! | 22N | CHURCH ST. | 138 | T61 | 15/20/25 | 26.4 | 27.93 | 21.1516 | 22.2878 | 20.3112 | 25 | 111.7% | 4 | 6.9825 | 152.7026 | 27.93 | 0 | 0 | 0 | 27.93 | y | y | y | R | 556 |  | 1 |  |  | 242 | 46.55% | 1 | 1 | 4
#REF! | 30N | MACCAN | 138 | T61 | 10/13.3/16.6//18.6 | 25.5 | - | 10.3785 | 3.4558 | 3.6603 | 18.6 | 55.8% | 2 | 5.1893 | 117.4911 | 0 | 0 | 0 | 0 | 0 | y | y | n | N | 556 |  | 2 |  |  | 426 | - | 1 | 1 | 0
#REF! | 37N | PARRSBORO | 69 | T51 | 8.4/11.2 | 25 | 7.91 | 7.2111 | 7.1058 | 6.2848 | 11.2 | 70.62% | 4 | 1.9775 | 45.6684 | 0 | 0 | 0 | 0 | 0 | y | n | n | R | 556 | 1 |  |  |  | 284 | 13.18% | 1 | 0 | 0
#REF! | 50N+ | TRENTON | 69 | T13 | 15/20/25//28 | 26.4 | 27.76 | 23.0253 | 18.1411 | 22.6156 | 18 | 154.2% | 4 | 6.94 | 151.7731 | 27.76 | 23.0253 | 0 | 22.6156 | 27.76 | y | y | y | N | 556/795/ 1113 |  | 4 |  |  | 1069 | - | 1 | 1 | 4
#REF! | 50N | TRENTON | 69 | T51 | 15/20//22.4 | 13.8 | 0.53 | 1.95 | 1.6308 | 1.5812 | 22.4 | 8.705% | 1 | 1.95 | 81.5821 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 1
#REF! | 55N | PICTOU TOWN | 69 | T1 | 5/6.7//7.5 | 4.16 | 4.73 | 4.194 | 4.9655 | 1.8458 | 7.5 | 66.21% | 4 | 1.2414 | 172.2848 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 11.03% | 0 | 0 | 0
#REF! | 56N | HALIBURTON | 69 | T1 | 7.5/10//11.2 | 25 | 14.46 | 9.6772 | 14.096 | 6.6359 | 11.2 | 129.1% | 3 | 4.82 | 111.3131 | 14.46 | 0 | 14.096 | 0 | 14.46 | y | y | n | R | 336/4/0 | 1 |  |  |  | 60 | 32.38% | 1 | 1 | 0 | Unit derated
| 62N | BRIDGE AVENUE | 69 | T1 | 15/20//22.4 | 25 | 41.74 | 39.452 | 35.7692 | 43.5636 | 44.8 | 97.24% | 6 | 7.2606 | 167.6764 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 | 2 |  |  |  | 127 | - | 1 | 1 | 6
| 62N | BRIDGE AVENUE | 69 | T2 | 15/20//22.4 | 25 | [15 empty] | y | y | [9 empty] | 1
| 74N | SPRINGHILL | 138 | T61 | 10/13.3/16.6//18.6 | 23 | 8.88 | 8.9674 | 8.4841 | 5.1837 | 18.6 | 48.21% | 2 | 4.4837 | 112.5505 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556/1113 |  | 3 |  |  | 789 | - | 1 | 1 | 2
| 81N | DEBERT | 138 | T61 | 15/20/25 | 26.4 | 17.81 | 17.4656 | 15.0586 | 16.9348 | 25 | 71.24% | 2 | 8.905 | 194.7464 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 1113 |  | 2 |  |  | 363 | - | 0 | 0 | 0
| *15N-T3 experiences elevated levels of gas if loaded over 18MVA |  |  |  |  | Totals | 278.68 | 250.6405 | 236.183 | 235.2213 | 405.73 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 95.71 | 49.5241 | 32.4176 | 46.275 | 96.6488 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [7 empty] | 9 | 14 | 22
+50N-T3 experiences elevated levels of gas if loaded over 18MVA
Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW.
|  | Notes: | [6 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year
Weather taken from Halifax Int A Station Gov. of Canada Website
56N-T1 to be replaced with 15/20/25 MVA unit in 2020
15N-T3 to be replaced with 15/20/25 MVA unit in 2020
Note on K15: Bryce Clothier: Manual update from load check
Note on L15: Bryce Clothier: Manual update from load check
Note on K16: Bryce Clothier: Manual update from load check
Note on L16: Bryce Clothier: Manual update from load check
Note on K25: Bryce Clothier: Calc currently not accounting for FORCE
Note on L25: Bryce Clothier: Calc currently not accounting for FORCE

## Sydney
SYDNEY OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: - 13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  | Subs | xfms | Feeders
1 | 3S | GANNON ROAD | 69 | T3 | 15/20 | 25 | 6 | 4.1 | 4.5228 | 2.6768 | 20 | 30% | 2 | 3 | 69.282 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 |  | 2 |  |  | 407 | - | 1 | 1 | 2
2 | 3S | GANNON ROAD | 69 | T4 | 10/13.3//14.9 | 12.47 | 7.56 | 12.94 | 13.3007 | 13.5424 | 14.9 | 90.89% | 3 | 4.5141 | 209.0012 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 3
3 | 3S | GANNON ROAD | 69 | T5 | 15/20/25//28 | 13.2 | 8.63 | 0 | 2.1916e-06 | 9.92 | 28 | 35.43% | 3 | 3.3067 | 144.6292 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 3
#REF! | 4S | TOWNSEND STREET | 69 | T52 | 15/20/22//24.6 | 12.47 | 33.41 | 33.43 | 34.4521 | 24.6922 | 47 | 73.3% | 8 | 4.3065 | 199.3876 | 0 | 0 | 0 | 0 | 0 | y | n | n | N | 2/0/556/4/0 | 3 |  |  |  | 187 | - | 1 | 0 | 0
#REF! | 4S | TOWNSEND STREET | 69 | T53 | 15/20//22.4 | 12.47 | [15 empty] | n | n | [9 empty] | 0
#REF! | 6S | TERRACE STREET | 69 | T1 | 7.5/10 | 4.16 | 3.89 | 7.0232 | 2.8563 | 0.40018 | 10 | 70.23% | 3 | 0.13339 | 18.513 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 556 | 2 |  |  |  | 164 | - | 0 | 0 | 0
#REF! | 11S | KELTIC DRIVE | 69 | T51 | 10/13.3//14.9 | 12.47 | 7.54 | 10.2327 | 8.2735 | 1.3109 | 14.9 | 68.68% | 3 | 3.4109 | 157.9217 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 2/0/556 | 2 |  |  |  | 116 | - | 0 | 0 | 0
#REF! | 11S | KELTIC DRIVE | 69 | T52 | 10/13.3//14.9 | 12.47 | 9.42 | 12.7841 | 11.7208 | 1.5179 | 14.9 | 85.8% | 3 | 4.2614 | 197.2973 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
#REF! | 11S | KELTIC DRIVE | 69 | T53 | 15/20/25.0 | 26.4 | 16.25 | 22.0532 | 15.6606 | 2.1803 | 25 | 88.21% | 2 | 11.0266 | 241.1446 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
#REF! | 15S | NEW WATERFORD | 69 | T1 | 10/13.3//14.9 | 12.47 | - | 11.7848 | 9.5498 | 10.8709 | 14.9 | 79.09% | 3 | 3.9283 | 181.8755 | 0 | 0 | 0 | 0 | 0 | n | n | y | N | 4/0/336 | 2 |  |  |  | 90 | - | 0 | 0 | 3
#REF! | 57S | ALBERT BRIDGE | 69 | T1 | 7.5/10//11.2 | 24.94 | 9.02 | 8.8098 | 8.4422 | 9.4644 | 11.2 | 84.5% | 2 | 4.7322 | 109.5485 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 27.84% | 0 | 0 | 0
#REF! | 81S | RESERVE STREET | 69 | T1 | 10/13.3/14.9 | 12.47 | 8.696 | 12.8393 | 11.1629 | 11.2 | 14.9 | 86.17% | 3 | 4.2798 | 198.1492 | 0 | 0 | 0 | 0 | 0 | y | n | n | N | 336 | 2 |  |  |  | 120 | - | 1 | 0 | 0
#REF! | 81S | RESERVE STREET | 69 | T2 | 15/20/25//28 | 13.2 | 13.35 | 19.7107 | 17.1371 | 17.19 | 28 | 70.4% | 4 | 4.9277 | 215.5301 | 0 | 0 | 0 | 0 | 0 |  | n | n | [9 empty] | 0 | 0
#REF! | 82S | WHITNEY PIER | 69 | T1 | 10/13.3//14.9 | 12.47 | 7.85 | 8.1755 | 5.084 | 5.6354 | 14.9 | 54.87% | 3 | 2.7252 | 126.1725 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 336 | 2 |  |  |  | 112 | - | 0 | 0 | 0
#REF! | 84S | V. J. DISTRIBUTION | 69 | T1 | 15/20/25//28 | 13.2 | 8.6 | 8.4885 | 7.227 | 6.1909 | 28 | 30.71% | 3 | 2.8667 | 125.3841 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 336 | 2 |  |  |  | 120 | - | 0 | 0 | 0
#REF! | 85S | WRECK COVE ** | 138 | T11 | 7.5/10//11.2 | 26.4 | 5.04 | 5.9157 | 5.4891 | 5.3808 | 11.2 | 52.82% | 2 | 2.9578 | 64.6857 | 0 | 0 | 0 | 0 | 0 | y | y | n | N | 556 |  | 2 |  |  | 368 | - | 1 | 1 | 0
#REF! | 104S | BADDECK | 138 | T61 | 7.5/10/12.5 | 13.2 | 10.95 | 6.7838 | 5.5961 | 7.1459 | 12.5 | 87.6% | 3 | 3.65 | 159.6461 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 |  | 1 |  |  | 60 | 18.25% | 0 | 0 | 0
#REF! | 111S | PRIME BROOK | 138 | T61 | 15/20/25.0 | 13.2 | - | - | - | 11.95 | - | 0% | 4 | 2.9875 | 130.6692 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 |  | 2 |  |  | 484 | - | 1 | 1 | 4
[6 empty] | Totals | 156.206 | 185.0713 | 160.475 | 141.2692 | 310.3 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [7 empty] | 5 | 5 | 15
Notes:
|  | Weather taken from Halifax Int A Station Gov. of Canada Website | [21 empty] | Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW.
|  | 111S-Prime Brook new in 2017. PI Data not available during 2019 peak. | [6 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year
|  | 111S-T61 - add 25MVA of transformer capacity in 2017 to cell P27 value | [6 empty] | 111S-T61 | 25 | 335.3 | Add 25MVA of transformer capacity at111S-Prime Brook |  |  |  | 2017
Note on K13: Bryce Clothier: Calc not currently accounting for 111S
Note on L13: Bryce Clothier: Calc not currently accounting for 111S

## Valley
VALLEY OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: - 13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  | Subs | xfms | Feeders
1 | 1V | AVON NO.1 ** | 69 | T51 | 7.5/10//11.2 | 24.94 | 11.4 | 0.88322 | 5.7684 | 3.323 | 11.2 | 101.8% | 1 | 11.4 | 263.9051 | 11.4 | 0.88322 | 5.7684 | 3.323 | 11.4 | y | y | n | R | 4/0 | 1 |  |  |  | 45 | 25.33% | 1 | 1 | 0
#REF! | 12V | LEQUILLE HYDRO | 69 | T2 | 7.5/10//11.2 | 12.47 | 5.14 | 7.0384 | 7.8782 | 10.1654 | 11.2 | 90.76% | 3 | 3.3885 | 156.8837 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 556 | 2 |  |  |  | 169 | - | 1 | 1 | 3
#REF! | 13V | GULCH ** | 69 | T51 | 7.5/10 | 13.8 | 3.18 | 3.9415 | 3.7676 | 3.2429 | 10 | 39.42% | 1 | 3.9415 | 164.9017 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 2/0/556 | 3 |  |  |  | 169 | - | 1 | 1 | 1
| 14V | RIDGE HYDRO | 69 | T1 | 5 | 6.9 | - | 0.2516 | 0.37267 | 0.32739 | 5 | 7.453% | 1 | 0.37267 | 31.1826 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 2/0 | 2 |  |  |  | 68 | - | 0 | 0 | 0
#REF! | 16V | WEYMOUTH HYDRO | 69 | T51 | 7.5/10//11.2 | 12.47 | 7.84 | 7.3413 | 7.0024 | 6.332 | 11.2 | 70% | 2 | 3.92 | 181.4926 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 2/0 | 1 |  |  |  | 34 | 62.82% | 1 | 1 | 2
#REF! | 18V | UPPER BURLINGTON | 69 | T51 | 7.5/10/12.5 | 26.4 | 9.73 | 9.6505 | 7.5938 | 7.027 | 12.5 | 77.84% | 3 | 3.2433 | 70.9295 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 1/0 | 1 |  |  |  | 29 | 33.55% | 0 | 0 | 0
#REF! | 20V | FIVE POINTS | 69 | T52 | 5//5.6 | 12.47 | 4.8 | 4.8 | 4.7999 | 5.4176 | 5.6 | 96.74% | 1 | 5.4176 | 250.8299 | 0 | 0 | 0 | 0 | 0 | y | y | y | N | 336 | 2 |  |  |  | 120 | - | 1 | 1 | 1
#REF! | 22V | NEW MINAS | 69 | T51 | 7.5/12.5 | 13.2 | 6.56 | 8.2857 | 7.6578 | 9.3156 | 12.5 | 74.52% | 3 | 3.1052 | 135.8168 | 0 | 0 | 0 | 0 | 0 | n | n | y | R | 336 | 1 |  |  |  | 60 | 51.97% | 0 | 0 | 3
#REF! | 22V | NEW MINAS | 69 | T52 | 7.5/10/12.5//14 | 13.2 | 9.7 | 8.2857 | 8.7745 | 9.7206 | 14 | 69.43% | 3 | 3.2402 | 141.7219 | 0 | 0 | 0 | 0 | 0 |  | n | y | [9 empty] | 0 | 3
#REF! | 36V | HILLATON | 69 | T1 | 7.5/10//11.2 | 12.47 | 6 | 7.2967 | 12.1472 | 6.279 | 11.2 | 108.5% | 3 | 4.0491 | 187.4676 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 60 | 20.25% | 0 | 0 | 0 | Value not counted: Was used as emergency supply to adjacent feeder
#REF! | 50V | KLONDIKE | 69 | T51 | 15/20/25 | 26.4 | 21.62 | 20.3247 | 22.6528 | 21.9468 | 25 | 90.61% | 2 | 11.3264 | 247.7003 | 21.62 | 20.3247 | 22.6528 | 21.9468 | 22.6528 | y | n | n | R | 1 | 1 |  |  |  | 24 | 94.39% | 1 | 0 | 0 | Line to Klondike was uprated to 70C operating temp in 2020, raising top rating to 30MVA from 24MVA
#REF! | 51V | TREMONT | 69 | T51 | 7.5/10.0 | 13.2 | 4.8 | 5.7616 | 3.4375 | 4.0429 | 10 | 57.62% | 1 | 5.7616 | 252.004 | 0 | 0 | 0 | 0 | 0 | y | n | n | N | 4/0/556 | 2 | 2 |  |  | 630 | - | 1 | 0 | 0
#REF! | 52V | BERWICK | 69 | T51 | 5/6.67/7.47 | 4.16 | - | - | - | 3.5938 | 7.47 | 48.11% | 3 | 1.1979 | 166.256 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 7.986% | 0 | 0 | 0 | Town of Berwick - Not Counted, Customer Owned
#REF! | 55V | WATERVILLE | 69 | T51 | 8.4/11.2/14 | 13.2 | 5.14 | 6.3571 | 8.1961 | 8.3503 | 14 | 59.64% | 2 | 4.1751 | 182.6148 | 0 | 0 | 0 | 0 | 0 | n | y | y | R | 4/0 | 2 |  |  |  | 45 | 46.54% | 0 | 1 | 2
| 55V | WATERVILLE | 69 | T52 | 7.5/10//11.2 | 12.47 | 10.18 | 12.5906 | 10.6549 | 6.342 | 11.2 | 112.4% | 2 | 6.2953 | 291.4671 | 10.18 | 12.5906 | 10.6549 | 6.342 | 12.5906 |  | y | y | [9 empty] | 1 | 2
#REF! | 63V | KINGSTON | 69 | T51 | 15/20//25 | 13.2 | 15.39 | 12.9674 | 14.5058 | 12.9301 | 25 | 61.56% | 3 | 5.13 | 224.3793 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 45 | 34.2% | 0 | 0 | 0
#REF! | 64V | GREENWOOD VILL. | 69 | T51 | 7.5/10/12.5//14 | 13.2 | 8.96 | 7.2942 | 9.5294 | 7.9862 | 14 | 68.07% | 3 | 3.1765 | 138.9339 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 21.18% | 0 | 0 | 0
#REF! | 65V | MIDDLETON RURAL | 69 | T1 | 7.5/10//11.2 | 12.47 | - | 13.938 | 14.0613 | 11.1861 | 11.2 | 125.5% | 3 | 4.6871 | 217.0082 | 0 | 13.938 | 14.0613 | 0 | 14.0613 | y | y | n | R | 336 | 1 |  |  |  | 60 | 23.44% | 1 | 1 | 0
#REF! | 70V | BRIDGETOWN RURAL | 69 | T51 | 7.5//8.4 | 12.48 | 8.68 | 7.5784 | 7.8316 | 7.8052 | 8.4 | 103.3% | 2 | 4.34 | 200.7773 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 60 | 14.47% | 0 | 0 | 0
#REF! | 74V | CORNWALLIS | 69 | T51 | 3/4//4.48 | 12.47 | - | 2.046 | 0.93234 | 1.7527 | 4.48 | 45.67% | 2 | 1.023 | 47.3651 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2 | 1 |  |  |  | 24 | 8.525% | 0 | 0 | 0
#REF! | 76V | MAITLAND BRIDGE | 69 | T1 | 1 | 12.5 | - | 0.54343 | 1.3975 | 1.3587 | 1 | 139.8% | 1 | 1.3975 | 64.5479 | 0 | 0 | 1.3975 | 1.3587 | 1.3975 | n | n | n | N | 4/0 | 2 |  |  |  | 68 | - | 0 | 0 | 0
#REF! | 77V | CONWAY | 69 | T1 | 7.5/10//11.2 | 12.48 | 12.95 | 11 | 12.6202 | 11.9832 | 11.2 | 115.6% | 3 | 4.3167 | 199.6978 | 12.95 | 0 | 12.6202 | 11.9832 | 12.95 | y | n | y | R | 4/0 | 1 |  |  |  | 45 | 37.37% | 1 | 0 | 3
#REF! | 77V | CONWAY | 69 | T52 | 5//6.7 | 26.4 | 3.2 | 3.2 | 3.8675 | 2.8435 | 6.7 | 57.72% | 1 | 3.8675 | 84.5793 | 0 | 0 | 0 | 0 | 0 |  | n | y | [9 empty] | 0 | 1
#REF! | 79V | THREE MILE PLAINS | 69 | T1 | 15/20/25//28 | 26.4 | 28.6 | 33.589 | 23.2892 | 31.2765 | 28 | 120% | 3 | 11.1963 | 244.8559 | 0 | 33.589 | 0 | 31.2765 | 33.589 | y | y | y | N | 4/0/336 | 3 |  |  |  | 165 | - | 1 | 1 | 3
| 82V | ELMSDALE | 138 | T1 | //28/37.3/46.7 | 26.4 | - | 31.1 | 36.7515 | 38.6913 | 46.7 | 82.85% | 3 | 12.8971 | 282.0508 | - | 31.1 | 36.7515 | 38.6913 | 38.6913 | y | y | y | N | 556 |  | 2 |  |  | 368 | - | 1 | 1 | 3
#REF! | 82V | ELMSDALE | 138 | T62 | //25/33/42.0 | 26.4 | - | 18.37 | 17.9978 | 17.5929 | 42 | 43.74% | 2 | 9.185 | 200.8698 | 0 | 0 | 0 | 0 | 0 |  | y | y | [9 empty] | 1 | 2
#REF! | 83V | WOLFVILLE RIDGE | 69 | T51 | 7.5/10//11.2 | 12.47 | - | 14.5765 | 14.2515 | 13.2353 | 11.2 | 130.1% | 3 | 4.8588 | 224.9596 | 0 | 14.5765 | 14.2515 | 13.2353 | 14.5765 | n | n | n | R | 336 | 1 |  |  |  | 60 | 24.29% | 0 | 0 | 0
#REF! | 93V | SAULNIERVILLE | 69 | T51 | 7.5/10/12.5 | 13.2 | 13.52 | 11.0142 | 13.4525 | 13.064 | 12.5 | 108.2% | 4 | 3.38 | 147.8367 | 13.52 | 0 | 13.4525 | 0 | 13.52 | y | n | n | R | 2/0/556 | 1 |  |  |  | 34 | 39.76% | 1 | 0 | 0
| 99V | HIGHBURY | 138 | T61 | 15/20/25.0 | 13.2 | 15.95 | 15.9157 | 16.6757 | 16.3972 | 25 | 66.7% | 4 | 4.1689 | 182.3429 | 0 | 0 | 0 | 0 | 0 | y | y | y | R | 556 | 1 |  |  |  | 165 | 27.79% | 1 | 1 | 4
[6 empty] | Totals | 213.34 | 285.9415 | 297.8675 | 293.529 | 419.45 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 69.67 | 127.002 | 131.6106 | 128.1568 | 175.4289 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [7 empty] | 13 | 12 | 33
Notes:
|  | 50V-T51 is limited by the transmission line 18MVA Summer and 26 MVA Winter | [21 empty] | Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW.
|  | 77V-T52 was replaced in 2019 with 5/6.67MVA unit | [6 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year
|  | 65V-T1 to have extra cooling stage added to increase top rating to 14 MVA in 2020 | [6 empty] | 2H-T62 | 46.7 | 423.12 | Add 46.7MVA of transformer capacity iat 2H |  |  |  | 2019
|  | 83V-T51 to have extra cooling stage added to increase top rating to 14 MVA in 2020 | [6 empty] | 77V-T52 | 3 | 426.12 | 3MVA transformer replaced with 5//6.7 MVA unit |  |  |  | 2019
Note on K19: Bryce Clothier: Added 53V Berwick North to the calculation, assume it has 40% of the load - based on xfmr sizes
Note on L19: Bryce Clothier: Added 53V Berwick North to the calculation, assume it has 40% of the load - based on xfmr sizes

## Western
WESTERN OPERATING AREA
| SUBSTATION I.D. |  | TRANSFORMER DATA |  |  |  | Measured MVA |  |  |  | Loading |  | # Feeders - 2020 |  |  | Constrained |  |  |  |  | SCADA |  |  | Transmission Supply
| Sub | Substation | HV | Xfmr | Xfmr | LV | 2017-01-01 | 2018-01-07 17:00 | 2019-02-27 07:45 | 2020-01-17 18:10 | Top rating | % Loaded | No. of Feeders | Avg. MVA | Current | 2017 | 2018 | 2019 | 2020 | Max | Sub (y/n) | Xfmrs (y/n) | Fdrs (Y/N) | Radial? | Size | # of Lines |  |  |  | Line Capacity | Radial Line % Loaded |  | SCADA
| No. | Name | kV | I.D. | Rating | kV | Load Check | Temp: - 13.6oC | Temp: -16.4oC | Temp: -14.3oC | [5 empty] | MVA | MVA | MVA | MVA | MVA |  |  |  | (R / N) | ACSR | 69kV | 138kV | 230kV | 345kV | Total Winter MVA |  | Subs | xfms | Feeders
#REF! | 16W | HEBRON | 69 | T51 | 7.5/10/12.5 | 13.2 | - | 13.1359 | 10.1776 | 9.4709 | 12.5 | 105.1% | 2 | 6.568 | 287.2742 | - | 13.1359 | 10.1776 | 9.4709 | 13.1359 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 80.71% | 0 | 0 | 0 | Loop supply exists already
#REF! | 19W | CENTRAL ARGYLE | 69 | T51 | 5//5.6 | 12.48 | 6.51 | 5.6254 | 6.5428 | 6.5135 | 5.6 | 116.8% | 2 | 3.2714 | 151.3418 | 6.51 | 0 | 6.5428 | 6.5135 | 6.5428 | n | n | n | R | 336 | 1 |  |  |  | 60 | 47.58% | 0 | 0 | 0
#REF! | 20W | LWR. EAST PUBNICO | 69 | T51 | 3/4//4.48 | 12.47 | 3.65 | 3.4916 | 3.6747 | 3.1703 | 4.48 | 82.03% | 2 | 1.8374 | 85.0684 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 60 | 36.68% | 0 | 0 | 0
#REF! | 21W | LWR. WOOD'S HBR. | 69 | T51 | 5//5.6 | 12.48 | - | 3.2976 | 2.6888 | 2.9371 | 5.6 | 58.89% | 2 | 1.6488 | 76.2778 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 60 | 30.55% | 0 | 0 | 0
#REF! | 22W | BARRINGTON PASS. | 69 | T51 | 7.5/10/12.5//14 | 13.2 | 14.85 | 15.0334 | 12.9064 | 12.7591 | 14 | 107.4% | 3 | 5.0111 | 219.1796 | 14.85 | 15.0334 | 0 | 0 | 15.0334 | n | y | y | R | 4/0 | 1 |  |  |  | 45 | 33.41% | 0 | 1 | 3
#REF! | 23W | CLYDE RIVER | 69 | T1 | 3.75/5//5.6 | 12.47 | - | 4.7404 | 3.8179 | 3.2875 | 5.6 | 84.65% | 2 | 2.3702 | 109.7377 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 43.94% | 0 | 0 | 0
#REF! | 25W | OHIO RD. ** | 69 | T1 | 7.5/10//11.2 | 12.47 | - | 8.7747 | 11.1065 | 8.3682 | 11.2 | 99.17% | 3 | 3.7022 | 171.4078 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 24.68% | 0 | 0 | 0
#REF! | 36W | GREEN HARBOUR | 69 | T51 | 3.75/5//5.6 | 12.47 | - | 3.4117 | 4.5827 | 4.0764 | 5.6 | 81.83% | 2 | 2.2914 | 106.0883 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 4/0 | 2 |  |  |  | 45 | - | 0 | 0 | 0
#REF! | 37W | LOCKEPORT | 69 | T1 | 3.75/5//5.6 | 4.16 | - | 2.1323 | 2.7943 | 2.1187 | 5.6 | 49.9% | 3 | 0.93145 | 129.2723 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 6.21% | 0 | 0 | 0
#REF! | 46W | BROAD RIVER | 69 | T1 | 3.75/5//5.6 | 12.47 | 3.66 | 4.549 | 4.1356 | 2.9662 | 5.6 | 81.23% | 2 | 2.2745 | 105.3066 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 2 |  |  |  | 45 | 10.11% | 0 | 0 | 0
#REF! | 48W | WATERLOO STREET | 69 | T1 | 7.5/10//11.2 | 4.16 | 3.45 | 1.146 | 1.116 | 1.146 | 11.2 | 30.8% | 3 | 1.15 | 159.604 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 336 | 1 |  |  |  | 45 | 7.667% | 0 | 0 | 0
#REF! | 50W | MILTON | 69 | T53 | 7.5/10/12.5 | 26.4 | 12.93 | 12.0387 | 14.9994 | 12.0435 | 12.5 | 120% | 2 | 7.4997 | 164.0133 | 0 | 0 | 14.9994 | 0 | 14.9994 | y | y | n | N | 336-1113 |  | 5 |  |  | 1043 | - | 1 | 1 | 0
#REF! | 57W | CALEDONIA | 69 | T1 | 3 | 24 | - | 2.4191 | 1.118 | 1.8661 | 3 | 80.64% | 2 | 1.2095 | 29.0968 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 2/0 | 2 |  |  |  | 68 | - | 0 | 0 | 0
#REF! | 70W | HIGH ST (BRIDGEWTR) | 69 | T51 | 5/6.7 | 4.16 | 2.47 | 2.39 | 2.5411 | 2.2088 | 6.7 | 37.93% | 2 | 1.2705 | 176.3321 | 0 | 0 | 0 | 0 | 0 | n | n | y | R | 4/0 | 1 |  |  |  | 45 | 64.83% | 0 | 0 | 2
#REF! | 70W | HIGH ST (BRIDGEWTR) | 69 | T53 | 15/20/25 | 13.2 | 25.7 | 24.26 | 26.6303 | 23.1477 | 25 | 106.5% | 6 | 4.4384 | 194.1292 | 0 | 0 | 26.6303 | 0 | 26.6303 | [12 empty] | 0 | 0
#REF! | 73W | AUBURNDALE | 69 | T1 | 7.5/10//11.2 | 24.94 | 14.32 | 12.4241 | 14.2299 | 11.2205 | 11.2 | 127.9% | 2 | 7.16 | 165.7509 | 14.32 | 12.4241 | 14.2299 | 0 | 14.32 | n | n | y | R | 556 | 1 |  |  |  | 82 | 72.49% | 0 | 0 | 2
#REF! | 76W | MAHONE BAY | 69 | T1 | 3.75/5 | 4.16 | - | 2.3382 | 2.9747 | 3.4376 | 5 | 68.75% | 3 | 1.1459 | 159.0287 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 71.99% | 0 | 0 | 0
#REF! | 78W | MARTINS BROOK | 66 | T1 | 2.5/3 | 12.5 | - | 2.7712 | 3.5059 | 3.7322 | 3 | 124.4% | 2 | 1.8661 | 86.1917 | 0 | 0 | 3.5059 | 3.7322 | 3.7322 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 61.88% | 0 | 0 | 0
#REF! | 80W | INDIAN PATH | 69 | T1 | 5/6.7//7.5 | 12.47 | - | 7.594 | 8.7116 | 3.7199 | 7.5 | 116.2% | 3 | 2.9039 | 134.446 | 0 | 0 | 8.7116 | 0 | 8.7116 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 50.9% | 0 | 0 | 0
#REF! | 81W | LUNENBURG TOWN | 69 | T51 | 7.5/10/12.5 | 6.9 | - | 6.062 | 7.4367 | 8.5939 | 20.9 | 41.12% | 5 | 1.7188 | 143.8173 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 25.28% | 0 | 0 | 0
#REF! | 81W | LUNENBURG TOWN | 69 | T2 | 7.5//8.4 | 4.16 | [26 empty] | 0
#REF! | 84W | ROBINSON'S CORNER | 69 | T1 | 7.5/10/12.5//14 | 13.2 | 15.9 | 7.9994 | 7.4259 | 10.037 | 14 | 71.69% | 2 | 5.0185 | 219.5026 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 1/0 | 1 |  |  |  | 60 | 26.5% | 0 | 0 | 0 | Value not counted: Was used as emergency supply to adjacent feeder
#REF! | 87W | HUBBARDS | 138 | T61 | 7.5/10/12.5 | 13.2 | 10.37 | 6.8795 | 7.0723 | 5.7852 | 12.5 | 82.96% | 2 | 5.185 | 226.7849 | 0 | 0 | 0 | 0 | 0 | y | y | n | N | 556 |  | 2 |  |  | 407 | - | 1 | 1 | 0
#REF! | 88W | PLEASANT STREET | 69 | T51 | 15/20/25 | 13.2 | - | 17.6812 | 23.1824 | 17.2364 | 25 | 92.73% | 4 | 5.7956 | 253.4918 | 0 | 0 | 0 | 0 | 0 | y | y | y | R | 4/0 | 1 |  |  |  | 34 | 68.18% | 1 | 1 | 4
#REF! | 88W | PLEASANT STREET | 69 | T52 | 7.5/10//11.2 | 12.47 | 7.14 | 7.09 | 5.0674 | 4.0537 | 11.2 | 63.75% | 3 | 2.38 | 110.192 | 0 | 0 | 0 | 0 | 0 |  |  |  | R | 2/0 | 1 |  |  |  | 34 | 21% | 0 | 0 | 0
#REF! | 89W | BRIDGEWATER EAST | 138/69 | T51 | 15/20/25.0 | 12.47 | - | 13.1927 | 12.6072 | 9.0403 | 25 | 52.77% | 4 | 3.2982 | 152.7022 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 2/0 | 1 |  |  |  | 34 | 38.8% | 0 | 0 | 0
#REF! | 91W | MIDDLEFIELD | 69 | T51 | 5/6.67/8.33 | 23 | 7 | 2.7781 | 4.8447 | 4.0433 | 8.33 | 84.03% | 1 | 7 | 175.7153 | 0 | 0 | 0 | 0 | 0 | n | n | n | N | 2/0 | 2 |  |  |  | 68 | - | 0 | 0 | 0
#REF! | 92W | CARLETON | 69 | T1 | 2//2.24 | 12.47 | 1.51 | 2.941 | 1.9112 | 1.7255 | 2.24 | 131.3% | 1 | 2.941 | 136.1672 | 0 | 2.941 | 0 | 0 | 2.941 | n | n | n | N | 2/0 | 2 |  |  |  | 68 | - | 0 | 0 | 0
#REF! | 102W | TUSKET DISTRIBUTION | 69 | T51 | 7.5/10//11.2 | 12.48 | - | 7.192 | 6.5497 | 5.4067 | 11.2 | 64.21% | 2 | 3.596 | 166.3587 | 0 | 0 | 0 | 0 | 0 | n | n | n | R | 4/0 | 1 |  |  |  | 45 | 15.98% | 0 | 0 | 0
#REF! | 103W | GOLD RIVER | 138 | T61 | 7.5/10/12.5 | 13.2 | 7.42 | 13.119 | 6.5065 | 5.4367 | 12.5 | 105% | 2 | 3.71 | 162.2704 | 0 | 0 | 0 | 0 | 0 | n | n | y | N | 556 |  | 2 |  |  | 407 | 21.86% | 0 | 0 | 2 | Values not counted: circuit offloaded to Hubbards 87W
[6 empty] | Totals | 136.88 | 216.5081 | 220.8583 | 189.5486 | 303.75 |  | Constrained feeders > 260amps Constrained Xfmrs > 106% Top N/P |  |  | 35.68 | 43.5345 | 84.7975 | 19.7165 | 106.0466 |  |  |  | Network Stations: Line Capacity for Network stations only includes sum of winter MVA ratings for Network connected lines. | [7 empty] | 3 | 4 | 13
Notes:
|  | Weather taken from Halifax Int A Station Gov. of Canada Website | [21 empty] | Radial Stations: Radial lines can supply multiple substations. However, radial supply is limited to 60MW by NS Power's Radial Transmission Policy (CEJC). As such, radial line capacity is the lesser of the line rating and 60MW.
|  | 101W-Bowater to add distribution transformer and two 25kV feeders in 2020 | [6 empty] | Unit | MVA Change | New Total | Description |  |  |  | Year
19W-T51 scheduled for 7.5/10/12.5 MVA replacement in 2020