## 2024 - Peak Hour
Generation Resource | MW
Thermal | 1392
CT's | 226
Hydro | 168
Wind | 33
Tidal | 0
Biomass | 56
Maritime Link | 150
Maritime Link Imports | 7
Other Imports | 51
Battery | 0
System Peak (MW) and Time (HE) | February 21 @ 9AM

## 2030 - Winter Peak
2030 Peak Load Generation
Peak Load Hour
2030-01-08 18:00
2030 | Installed Capacity (MW)
| Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
| 0 | 462 | 600 | 150 | 231 | 374.36 | 9.42 | 74.88 | 2068.87 | 102 | 153 | 459 | 0 | 170 |  | 4854.53
Generation (GWh) Jan 7, 2030 - Jan 9, 2030 | [16 empty] | Curtailed Renewables (MW)
Date/Time | Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
2030-01-07 01:00 | 0 | 127.74 | 0 | 0 | 0 | 69.04 | 0 | 68.67 | 1096.53 | 0 | 0 | 0 | 0 | 0 | 500 | 1861.98 | 6.13
2030-01-07 02:00 | 0 | 264 | 0 | 0 | 0 | 106.44 | 1.59 | 74.8 | 800.05 | 0 | 0 | 0 | 0 | 0 | 575 | 1821.88 | 0
2030-01-07 03:00 | 0 | 462 | 0 | 0 | 0 | 74.34 | 4.18 | 74.8 | 626.21 | 0 | 0 | 0 | 0 | 0 | 575 | 1816.53 | 32.1
2030-01-07 04:00 | 0 | 414 | 0 | 0 | 0 | 69.04 | 5.26 | 71 | 704.51 | 0 | 0 | 0 | 0 | 0 | 575 | 1838.81 | 3.8
2030-01-07 05:00 | 0 | 462 | 0 | 30 | 0 | 90.54 | 4.18 | 74.8 | 553.91 | 0 | 0 | 0 | 0 | 0 | 575 | 1790.43 | 15.9
2030-01-07 06:00 | 0 | 462 | 0 | 107.92 | 0 | 199.44 | 1.63 | 74.8 | 199.9 | 0 | 0 | 0 | 0 | 82.38 | 575 | 1703.07 | 13
2030-01-07 07:00 | 0 | 462 | 0 | 118.53 | 0 | 106.44 | 0 | 74.8 | 447.42 | 0 | 0 | 0 | 0 | 7 | 575 | 1791.19 | 0
2030-01-07 08:00 | 0 | 462 | 50 | 120 | 0 | 192.44 | 1.81 | 74.8 | 526.63 | 0 | 113 | 0 | 0 | 4.46 | 400 | 1945.14 | 100
2030-01-07 09:00 | 0 | 462 | 300 | 120 | 0 | 278.44 | 2.72 | 74.8 | 320.02 | 0.36 | 193 | 0 | 0 | 9.89 | 325 | 2086.23 | 40
2030-01-07 10:00 | 0 | 462 | 250 | 107.92 | 0 | 196.44 | 2.99 | 74.8 | 384.48 | 30.82 | 121.42 | 0 | 0 | 0 | 400 | 2030.87 | 193.58
2030-01-07 11:00 | 0 | 462 | 200 | 107.92 | 0 | 305.44 | 2.83 | 74.8 | 369.65 | 17.2 | 125 | 0 | 0 | 8.43 | 400 | 2073.27 | 81
2030-01-07 12:00 | 0 | 462 | 150 | 107.92 | 0 | 185.04 | 1.45 | 74.8 | 375.55 | 18.93 | 125 | 0 | 0 | 0 | 450 | 1950.69 | 95.4
2030-01-07 13:00 | 0 | 462 | 200 | 120 | 0 | 199.44 | 0 | 74.8 | 294.27 | 4.26 | 193 | 0 | 0 | 14.7 | 375 | 1937.47 | 13
2030-01-07 14:00 | 0 | 462 | 150 | 107.92 | 0 | 199.44 | 0.75 | 74.8 | 351.64 | 3.74 | 193 | 0 | 0 | 7.91 | 375 | 1926.2 | 13
2030-01-07 15:00 | 0 | 462 | 200 | 120 | 0 | 229.13 | 4.41 | 74.8 | 325.07 | 4.98 | 113 | 0 | 0 | 0 | 450 | 1983.39 | 169.31
2030-01-07 16:00 | 0 | 462 | 500 | 116.5 | 0 | 209.31 | 5.28 | 74.8 | 199.08 | 1.46 | 193 | 0 | 0 | 0 | 375 | 2136.43 | 3.13
2030-01-07 17:00 | 0 | 462 | 600 | 111.2 | 0 | 273.62 | 4.2 | 74.8 | 131.28 | 0.01 | 125 | 30 | 0 | 126.72 | 450 | 2388.83 | 112.82
2030-01-07 18:00 | 0 | 462 | 600 | 128 | 0 | 313.47 | 1.91 | 74.8 | 92.15 | 0 | 193 | 122.4 | 0 | 160.18 | 325 | 2472.91 | 4.97
2030-01-07 19:00 | 0 | 462 | 500 | 107.92 | 0 | 307.44 | 0 | 74.8 | 175.5 | 0 | 175 | 122.4 | 0 | 146.39 | 350 | 2421.45 | 29
2030-01-07 20:00 | 0 | 462 | 600 | 107.92 | 0 | 200.07 | 0 | 74.8 | 252.75 | 0 | 117.58 | 122.4 | 0 | 46.21 | 400 | 2383.73 | 193.79
2030-01-07 21:00 | 0 | 462 | 250 | 107.92 | 0 | 307.44 | 1.46 | 74.8 | 486.25 | 0 | 193 | 122.4 | 0 | 5.63 | 325 | 2335.9 | 11
2030-01-07 22:00 | 0 | 462 | 0 | 110.49 | 0 | 106.44 | 2.94 | 74.8 | 822.51 | 0 | 125 | 122.4 | 0 | 0 | 450 | 2276.58 | 68
2030-01-07 23:00 | 0 | 462 | 0 | 107.92 | 0 | 69.04 | 3.06 | 74.8 | 825.91 | 0 | 150 | 117.26 | 0 | 0 | 350 | 2159.99 | 43
2030-01-08 | 0 | 213.75 | 0 | 52 | 0 | 67.04 | 2.83 | 43 | 1310.07 | 0 | 0 | 55 | 0 | 0 | 325 | 2068.69 | 8.81
2030-01-08 01:00 | 0 | 206.81 | 0 | 52 | 0 | 69.04 | 1.69 | 52 | 1407.72 | 0 | 0 | 55 | 0 | 0 | 275 | 2119.26 | 22.81
2030-01-08 02:00 | 0 | 206.74 | 0 | 52 | 0 | 69.04 | 0.56 | 43 | 1324.22 | 0 | 0 | 55 | 0 | 0 | 325 | 2075.56 | 6.81
2030-01-08 03:00 | 0 | 211.78 | 0 | 52 | 0 | 90.95 | 1.45 | 56.87 | 1069.98 | 0 | 0 | 55 | 0 | 0 | 475 | 2013.03 | 33.42
2030-01-08 04:00 | 0 | 206.18 | 0 | 52 | 0 | 69.04 | 2.81 | 52 | 1184.64 | 0 | 0 | 55 | 0 | 0 | 450 | 2071.67 | 22.81
2030-01-08 05:00 | 0 | 270.16 | 0 | 52 | 0 | 74.34 | 5.7 | 52 | 1106.82 | 0 | 0 | 55 | 0 | 0 | 475 | 2091.02 | 54.91
2030-01-08 06:00 | 0 | 393.55 | 0 | 91.79 | 0 | 106.44 | 5.7 | 68.67 | 684.5 | 0 | 0 | 55 | 0 | 0 | 575 | 1980.65 | 6.13
2030-01-08 07:00 | 0 | 462 | 0 | 107.92 | 0 | 151.44 | 2.72 | 74.8 | 445.7 | 0 | 0 | 119.15 | 0 | 134.71 | 575 | 2073.44 | 61
2030-01-08 08:00 | 0 | 462 | 0 | 107.92 | 0 | 298.66 | 0.48 | 74.8 | 530.14 | 0 | 125 | 119 | 0 | 20 | 400 | 2138 | 87.78
2030-01-08 09:00 | 0 | 462 | 200 | 107.92 | 0 | 289.26 | 1.73 | 74.8 | 440.35 | 3.8 | 193 | 122.4 | 0 | 0 | 325 | 2220.26 | 29.18
2030-01-08 10:00 | 0 | 462 | 350 | 107.92 | 0 | 297.72 | 2.73 | 74.8 | 306.22 | 59.32 | 125 | 122.4 | 0 | 0 | 400 | 2308.11 | 88.72
2030-01-08 11:00 | 0 | 462 | 550 | 107.92 | 0 | 192.44 | 3.22 | 74.8 | 281.6 | 26.7 | 125 | 0 | 0 | 88.84 | 400 | 2312.52 | 88
2030-01-08 12:00 | 0 | 462 | 533.17 | 107.92 | 0 | 232.14 | 2.81 | 74.8 | 284.5 | 46.38 | 125 | 0 | 0 | 0 | 450 | 2318.72 | 190
2030-01-08 13:00 | 0 | 369 | 0 | 107.92 | 0 | 354.14 | 1.45 | 74.8 | 465.31 | 39.69 | 125 | 0 | 0 | 43.89 | 450 | 2031.2 | 68
2030-01-08 14:00 | 0 | 369 | 50 | 107.92 | 0 | 221.74 | 1.07 | 74.8 | 580.03 | 54.36 | 175 | 0 | 0 | 0 | 400 | 2033.92 | 44.4
2030-01-08 15:00 | 0 | 369 | 0 | 134.58 | 0 | 142.14 | 1.46 | 74.8 | 722.72 | 67.22 | 193 | 0 | 0 | 0 | 375 | 2079.92 | 0
2030-01-08 16:00 | 0 | 369 | 50 | 120.32 | 0 | 354.14 | 2.81 | 74.8 | 641.58 | 23.68 | 193 | 0 | 0 | 0 | 375 | 2204.33 | 0
2030-01-08 17:00 | 0 | 369 | 100 | 107.92 | 0 | 246.16 | 6.09 | 74.8 | 813.73 | 0.01 | 193 | 0 | 0 | 160 | 375 | 2445.71 | 107.98
2030-01-08 18:00 | 0 | 369 | 0 | 114.37 | 0 | 354.14 | 6.09 | 74.8 | 1086.15 | 0 | 193 | 0 | 0 | 37 | 325 | 2559.55 | 0
2030-01-08 19:00 | 0 | 369 | 100 | 107.92 | 0 | 346.88 | 2.83 | 74.8 | 1008.08 | 0 | 193 | 0 | 0 | 0 | 325 | 2527.51 | 7.26
2030-01-08 20:00 | 0 | 369 | 150 | 107.92 | 0 | 330.47 | 0.73 | 74.8 | 803.04 | 0 | 125 | 0 | 0 | 139.33 | 400 | 2500.29 | 91.67
2030-01-08 21:00 | 0 | 369 | 50 | 124.77 | 0 | 142.14 | 0 | 74.8 | 1196.8 | 0 | 125 | 0 | 0 | 0 | 400 | 2482.51 | 68
2030-01-08 22:00 | 0 | 274.15 | 0 | 85.13 | 0 | 142.14 | 0.77 | 68.67 | 1560.06 | 0 | 127 | 0 | 0 | 0 | 150 | 2407.92 | 72.13
2030-01-08 23:00 | 0 | 228.55 | 0 | 52 | 0 | 141.73 | 2.71 | 52 | 1653.65 | 0 | 113 | 0 | 0 | 0 | 0 | 2243.64 | 103.22
2030-01-09 | 0 | 147 | 0 | 52 | 0 | 102.74 | 2.94 | 37.22 | 1684.82 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.72 | 8.81
2030-01-09 01:00 | 0 | 185.55 | 0 | 0 | 0 | 72.84 | 0 | 0 | 1476.19 | 0 | 0 | 0 | 0 | 0 | 100 | 1834.58 | 327.21
2030-01-09 02:00 | 0 | 211.75 | 0 | 0 | 0 | 72.84 | 0 | 0 | 1424.58 | 0 | 0 | 0 | 0 | 0 | 100 | 1809.17 | 371.98
2030-01-09 03:00 | 0 | 183.55 | 0 | 0 | 0 | 72.84 | 0 | 0 | 1158.29 | 0 | 0 | 0 | 0 | 140 | 100 | 1654.68 | 614.5
2030-01-09 04:00 | 0 | 211.75 | 0 | 0 | 0 | 72.66 | 1.59 | 0 | 1368.12 | 0 | 0 | 0 | 0 | 20 | 100 | 1774.12 | 397.39
2030-01-09 05:00 | 0 | 183.55 | 0 | 0 | 0 | 74.05 | 6.39 | 0 | 1408.64 | 0 | 0 | 0 | 0 | 20 | 100 | 1792.63 | 374.05
2030-01-09 06:00 | 0 | 195.53 | 0 | 0 | 0 | 80.91 | 0 | 0 | 1507.57 | 0 | 0 | 0 | 0 | 0 | 100 | 1884.01 | 283.17
2030-01-09 07:00 | 0 | 183.55 | 0 | 0 | 0 | 67.45 | 2.83 | 0 | 1474.78 | 0 | 0 | 0 | 0 | 140 | 100 | 1968.61 | 308.98
2030-01-09 08:00 | 0 | 211.75 | 0 | 0 | 0 | 71.27 | 1.97 | 0 | 1571.14 | 0 | 113 | 0 | 0 | 144.9 | 0 | 2114.03 | 204.5
2030-01-09 09:00 | 0 | 211.75 | 0 | 0 | 0 | 79.14 | 0 | 0 | 1558.46 | 1.95 | 113 | 0 | 0 | 140 | 0 | 2104.3 | 222.72
2030-01-09 10:00 | 0 | 211.75 | 0 | 0 | 0 | 79.14 | 1.59 | 0 | 1631.33 | 0.12 | 193 | 0 | 0 | 0 | 0 | 2116.93 | 6.81
2030-01-09 11:00 | 0 | 183.55 | 0 | 0 | 0 | 80.91 | 0 | 0 | 1597.2 | 1.14 | 113 | 0 | 0 | 16.93 | 0 | 1992.73 | 216.62
2030-01-09 12:00 | 0 | 183.55 | 0 | 0 | 0 | 75.14 | 3.28 | 0 | 1300.94 | 1.52 | 113 | 0 | 0 | 140 | 0 | 1817.43 | 490.14
2030-01-09 13:00 | 0 | 211.75 | 0 | 0 | 0 | 79.82 | 0 | 0 | 1459.32 | 33.38 | 113 | 0 | 0 | 16.93 | 0 | 1914.2 | 248.55
2030-01-09 14:00 | 0 | 211.75 | 0 | 0 | 0 | 80.91 | 2.66 | 0 | 1420.88 | 44.2 | 113 | 0 | 0 | 0 | 0 | 1873.4 | 242.92
2030-01-09 15:00 | 0 | 183.55 | 0 | 0 | 0 | 67.45 | 1.46 | 0 | 1407.51 | 42.99 | 113 | 0 | 0 | 16.93 | 0 | 1832.89 | 215.37
2030-01-09 16:00 | 0 | 222.69 | 0 | 0 | 0 | 79.14 | 1.02 | 0 | 1393.2 | 22.25 | 113 | 0 | 0 | 0 | 0 | 1831.3 | 86.81
2030-01-09 17:00 | 0 | 291 | 0 | 0 | 0 | 86.79 | 2.77 | 0 | 1147.71 | 0 | 193 | 0 | 0 | 59.7 | 100 | 1880.97 | 6.81
2030-01-09 18:00 | 0 | 291 | 200 | 0 | 0 | 86.79 | 7.54 | 0 | 1152.37 | 0 | 193 | 0 | 0 | 135.83 | 50 | 2116.53 | 6.81
2030-01-09 19:00 | 0 | 291 | 0 | 0 | 0 | 86.79 | 7.56 | 0 | 1277.75 | 0 | 193 | 0 | 0 | 128.01 | 50 | 2034.11 | 6.81
2030-01-09 20:00 | 0 | 291 | 0 | 0 | 0 | 86.79 | 2.77 | 0 | 1358.23 | 0 | 193 | 0 | 0 | 24.98 | 50 | 2006.77 | 6.81
2030-01-09 21:00 | 0 | 291 | 150 | 0 | 0 | 86.79 | 1.18 | 0 | 980.04 | 0 | 193 | 0 | 0 | 142.13 | 50 | 1894.14 | 6.81
2030-01-09 22:00 | 0 | 291 | 400 | 0 | 0 | 86.79 | 0 | 0 | 810.16 | 0 | 193 | 0 | 0 | 20 | 100 | 1900.95 | 6.81
2030-01-09 23:00 | 0 | 291 | 200 | 0 | 0 | 86.79 | 1.41 | 0 | 660.38 | 0 | 193 | 0 | 0 | 122.76 | 100 | 1655.34 | 6.81
2030-01-10 | 0 | 291 | 288.48 | 0 | 0 | 86.79 | 2.94 | 10 | 715.41 | 0 | 0 | 0 | 0 | 111.01 | 100 | 1605.63 | 6.81

## 2030 - Curtailment Peak
2030 Curtailment Peak Load Generation
Curtailment Peak Day
2030-07-05
2030 | Installed Capacity (MW)
| Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
| 0 | 462 | 600 | 150 | 231 | 374.36 | 9.42 | 74.88 | 2068.87 | 102 | 153 | 459 | 0 | 170 |  | 4854.53
Generation (GWh) July 4, 2030 - July 6, 2030 | [16 empty] | Curtailed Renewables (MW)
Date/Time | Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
2030-07-04 01:00 | 0 | 188.5 | 50 | 0 | 0 | 87.67 | 0 | 34.2 | 261.69 | 0 | 0 | 0 | 0 | 0 | 625 | 1247.06 | 75.12
2030-07-04 02:00 | 0 | 188.5 | 0 | 0 | 0 | 42.67 | 1.05 | 43 | 278.84 | 0 | 0 | 0 | 0 | 0 | 625 | 1179.06 | 12.57
2030-07-04 03:00 | 0 | 188.5 | 0 | 0 | 0 | 100.97 | 2.14 | 43 | 227.75 | 0 | 0 | 0 | 0 | 0 | 625 | 1187.36 | 61.82
2030-07-04 04:00 | 0 | 188.5 | 0 | 0 | 0 | 42.67 | 2.75 | 43 | 219.11 | 0 | 0 | 0 | 0 | 0 | 625 | 1121.03 | 14.12
2030-07-04 05:00 | 0 | 188.5 | 0 | 0 | 0 | 42.67 | 2.79 | 43 | 173.09 | 0 | 0 | 0 | 0 | 0 | 625 | 1075.05 | 14.12
2030-07-04 06:00 | 0 | 188.5 | 0 | 0 | 0 | 140.35 | 2.29 | 24.15 | 53.83 | 12.68 | 0 | 0 | 0 | 10 | 625 | 1056.8 | 22.44
2030-07-04 07:00 | 0 | 188.5 | 0 | 0 | 0 | 94.67 | 1.41 | 33 | 29.19 | 50.03 | 0 | 0 | 0 | 71.25 | 625 | 1093.05 | 95.22
2030-07-04 08:00 | 0 | 188.5 | 0 | 0 | 0 | 142.23 | 0 | 43 | 18.69 | 78.63 | 186.74 | 0 | 0 | 109.64 | 425 | 1192.43 | 132.82
2030-07-04 09:00 | 0 | 188.5 | 0 | 0 | 0 | 132.67 | 1.92 | 43 | 23.32 | 96.56 | 113 | 0 | 0 | 155.49 | 500 | 1254.46 | 216.12
2030-07-04 10:00 | 0 | 188.5 | 0 | 0 | 0 | 106.49 | 3.96 | 43 | 38.56 | 100 | 125 | 0 | 0 | 130 | 500 | 1235.51 | 124.3
2030-07-04 11:00 | 0 | 188.5 | 0 | 0 | 0 | 254.67 | 4.16 | 43 | 41.07 | 99.09 | 175 | 0 | 0 | 0 | 450 | 1255.49 | 32.12
2030-07-04 12:00 | 0 | 188.5 | 0 | 0 | 0 | 166.29 | 3.55 | 43 | 46.77 | 95.69 | 175 | 0 | 0 | 109.15 | 450 | 1277.95 | 120.5
2030-07-04 13:00 | 0 | 188.5 | 0 | 0 | 0 | 49.67 | 1.31 | 43 | 90.32 | 96.63 | 175 | 0 | 0 | 0 | 450 | 1094.43 | 35.42
2030-07-04 14:00 | 0 | 188.5 | 0 | 0 | 0 | 49.67 | 0 | 49.82 | 155.39 | 96.12 | 193 | 0 | 0 | 159.21 | 425 | 1316.71 | 7.05
2030-07-04 15:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 1.64 | 0 | 261.72 | 99.76 | 193 | 0 | 0 | 0 | 425 | 1211.29 | 6.82
2030-07-04 16:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 2.29 | 0 | 334.6 | 96.51 | 175 | 0 | 0 | 10 | 450 | 1298.57 | 24.82
2030-07-04 17:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 2.61 | 0 | 400.3 | 87.15 | 150 | 0 | 0 | 96.95 | 425 | 1392.18 | 49.82
2030-07-04 18:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 2.41 | 0 | 653.86 | 51.96 | 193 | 0 | 0 | 10 | 275 | 1416.4 | 6.82
2030-07-04 19:00 | 0 | 184.5 | 0 | 0 | 0 | 41.67 | 1.87 | 0 | 729.24 | 28.6 | 113 | 0 | 0 | 0 | 425 | 1523.88 | 86.82
2030-07-04 20:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 0 | 0 | 503.73 | 4.78 | 113 | 0 | 0 | 21.3 | 500 | 1372.98 | 86.82
2030-07-04 21:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 1.75 | 0 | 499.13 | 0 | 125 | 0 | 0 | 48.81 | 450 | 1354.86 | 74.82
2030-07-04 22:00 | 0 | 188.5 | 0 | 0 | 0 | 41.67 | 2.87 | 0 | 674.66 | 0 | 130.26 | 0 | 0 | 129.64 | 150 | 1317.6 | 69.56
2030-07-04 23:00 | 0 | 153.95 | 0 | 0 | 0 | 11.87 | 3.67 | 0 | 1003.96 | 0 | 113 | 0 | 0 | 0 | 0 | 1286.45 | 141.81
2030-07-05 | 0 | 162.1 | 0 | 0 | 0 | 1.67 | 3.6 | 0 | 1038.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.4 | 404.98
2030-07-05 01:00 | 0 | 279.5 | 0 | 30 | 0 | 0.16 | 0 | 33 | 777.46 | 0 | 0 | 0 | 0 | 0 | 150 | 1270.12 | 807.03
2030-07-05 02:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 0 | 33 | 640.5 | 0 | 0 | 0 | 0 | 0 | 150 | 1211.08 | 995.37
2030-07-05 03:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.25 | 0 | 33 | 610.2 | 0 | 0 | 0 | 0 | 0 | 150 | 1180.87 | 1063.15
2030-07-05 04:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.25 | 0 | 10 | 325.52 | 0 | 0 | 0 | 0 | 150 | 150 | 1023.19 | 1326.44
2030-07-05 05:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 0 | 33 | 552.43 | 0 | 0 | 0 | 0 | 10 | 150 | 1133.01 | 1102.47
2030-07-05 06:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.25 | 0 | 10 | 603.85 | 0.27 | 0 | 0 | 0 | 20 | 150 | 1171.79 | 1007.56
2030-07-05 07:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 0 | 43 | 378.78 | 4.3 | 0 | 0 | 0 | 150 | 150 | 1113.66 | 1213.23
2030-07-05 08:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 0 | 10 | 668.96 | 0 | 113 | 0 | 0 | 20 | 150 | 1349.38 | 1203.13
2030-07-05 09:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.09 | 0 | 33 | 719.12 | 38.11 | 113 | 0 | 0 | 20 | 0 | 1310.74 | 1072.42
2030-07-05 10:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 0 | 10 | 427.4 | 0 | 193 | 0 | 0 | 150 | 0 | 1167.82 | 1309.64
2030-07-05 11:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.09 | 0 | 10 | 706.86 | 0 | 113 | 0 | 0 | 20 | 150 | 1387.37 | 1268.03
2030-07-05 12:00 | 0 | 279.5 | 0 | 112.46 | 0 | 0 | 0 | 33 | 321.15 | 0 | 113 | 0 | 0 | 150 | 75 | 1084.11 | 1539.23
2030-07-05 13:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 0 | 10 | 255.45 | 0 | 144.29 | 0 | 0 | 150 | 150 | 1097.16 | 1685.73
2030-07-05 14:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.09 | 0 | 33 | 551.21 | 33.39 | 113 | 0 | 0 | 0 | 150 | 1268.11 | 1276.64
2030-07-05 15:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 0 | 33 | 512.17 | 0 | 193 | 0 | 0 | 20 | 150 | 1295.59 | 1198.53
2030-07-05 16:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 0.99 | 10 | 370.39 | 45.49 | 113 | 0 | 0 | 150 | 150 | 1227.29 | 856.24
2030-07-05 17:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 1.81 | 33 | 800.38 | 14.87 | 193 | 0 | 0 | 20 | 0 | 1450.64 | 281.2
2030-07-05 18:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.25 | 2.03 | 24.65 | 563.61 | 29.89 | 193 | 0 | 0 | 150 | 0 | 1350.85 | 380.39
2030-07-05 19:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.25 | 1.95 | 33 | 476.28 | 19.08 | 113 | 0 | 0 | 117 | 150 | 1297.98 | 781.75
2030-07-05 20:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 0 | 0 | 685.81 | 3 | 193 | 0 | 0 | 20 | 150 | 1439.39 | 537.47
2030-07-05 21:00 | 0 | 279.5 | 450 | 107.92 | 0 | 8.69 | 0 | 0 | 151.41 | 0 | 161.71 | 0 | 0 | 150 | 0 | 1309.23 | 1246.55
2030-07-05 22:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 0 | 0 | 660.03 | 0 | 193 | 0 | 0 | 20 | 150 | 1410.61 | 422.6
2030-07-05 23:00 | 0 | 279.5 | 0 | 107.92 | 0 | 0 | 2.09 | 0 | 512.16 | 0 | 193 | 0 | 0 | 150 | 0 | 1244.67 | 275.01
2030-07-06 | 0 | 279.5 | 0 | 107.92 | 0 | 0.16 | 2.66 | 0 | 449.78 | 0 | 0 | 0 | 0 | 157 | 150 | 1147.02 | 552.07
2030-07-06 01:00 | 0 | 47 | 0 | 0 | 0 | 1.57 | 2.96 | 0 | 1164.56 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.09 | 239.79
2030-07-06 02:00 | 0 | 53.54 | 0 | 0 | 0 | 2.83 | 0 | 0 | 1116.44 | 0 | 0 | 0 | 0 | 0 | 0 | 1172.81 | 466.58
2030-07-06 03:00 | 0 | 45 | 0 | 0 | 0 | 5.77 | 0 | 0 | 1058.28 | 0 | 0 | 0 | 0 | 20 | 0 | 1129.05 | 508.71
2030-07-06 04:00 | 0 | 45 | 0 | 0 | 0 | 1.47 | 0.54 | 0 | 856.65 | 0 | 0 | 0 | 0 | 79.8 | 0 | 983.46 | 445.5
2030-07-06 05:00 | 0 | 45 | 0 | 0 | 0 | 1.47 | 1.65 | 0 | 836.73 | 0 | 0 | 0 | 0 | 93.45 | 0 | 978.3 | 248.36
2030-07-06 06:00 | 0 | 45 | 0 | 0 | 0 | 1.57 | 2.47 | 0 | 765.8 | 9.9 | 0 | 0 | 0 | 150 | 0 | 974.74 | 451.77
2030-07-06 07:00 | 0 | 47 | 0 | 0 | 0 | 1.47 | 2.56 | 0 | 1063.11 | 27.04 | 0 | 0 | 0 | 0 | 0 | 1141.18 | 193.78
2030-07-06 08:00 | 0 | 0 | 0 | 0 | 0 | 0.26 | 1.81 | 0 | 1008.51 | 52.05 | 113 | 0 | 0 | 20 | 0 | 1195.63 | 190.37
2030-07-06 09:00 | 0 | 0 | 0 | 0 | 0 | 4.78 | 1 | 0 | 1052.7 | 88.8 | 113 | 0 | 0 | 20 | 0 | 1280.28 | 197.53
2030-07-06 10:00 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 861.29 | 92.55 | 113 | 0 | 0 | 150 | 0 | 1217.09 | 487.52
2030-07-06 11:00 | 0 | 0 | 0 | 0 | 0 | 4.78 | 2.09 | 0 | 1119.57 | 61.95 | 113 | 0 | 0 | 20 | 0 | 1321.39 | 190.75
2030-07-06 12:00 | 0 | 0 | 0 | 0 | 0 | 4.78 | 2.87 | 0 | 865.66 | 96.89 | 113 | 0 | 0 | 150 | 0 | 1233.2 | 385.55
2030-07-06 13:00 | 0 | 0 | 0 | 0 | 0 | 0.25 | 3.09 | 0 | 860.94 | 93.69 | 113 | 0 | 0 | 0 | 0 | 1070.97 | 108.68
2030-07-06 14:00 | 0 | 0 | 0 | 0 | 0 | 5.77 | 2.87 | 0 | 784.98 | 101.22 | 148.71 | 0 | 0 | 0 | 0 | 1043.55 | 51.11
2030-07-06 15:00 | 0 | 0 | 0 | 0 | 0 | 4.75 | 2.03 | 0 | 650.56 | 101.94 | 193 | 0 | 0 | 0 | 0 | 952.28 | 6.82
2030-07-06 16:00 | 0 | 44.5 | 0 | 0 | 0 | 5.97 | 0.09 | 0 | 505.17 | 97.41 | 186.97 | 0 | 0 | 0 | 150 | 990.11 | 12.85
2030-07-06 17:00 | 0 | 44.5 | 0 | 0 | 0 | 5.97 | 1.35 | 0 | 372.62 | 62.61 | 193 | 0 | 0 | 142.85 | 275 | 1097.9 | 6.82
2030-07-06 18:00 | 0 | 44.5 | 291.4 | 0 | 0 | 5.97 | 2.56 | 2.79 | 179.98 | 48.45 | 193 | 0 | 0 | 163.6 | 250 | 1182.25 | 4.04
2030-07-06 19:00 | 0 | 44.5 | 185.74 | 0 | 0 | 5.97 | 2.8 | 0 | 297.3 | 19.49 | 193 | 0 | 0 | 162.45 | 275 | 1186.25 | 6.82
2030-07-06 20:00 | 0 | 44.5 | 97.91 | 0 | 0 | 5.97 | 2.75 | 0 | 395.31 | 1.08 | 193 | 0 | 0 | 155 | 275 | 1170.52 | 6.82
2030-07-06 21:00 | 0 | 44.5 | 0 | 0 | 0 | 5.97 | 1.81 | 0 | 731.37 | 0 | 193 | 0 | 0 | 1.7 | 175 | 1153.35 | 6.82
2030-07-06 22:00 | 0 | 0 | 0 | 0 | 0 | 5.97 | 0.45 | 0 | 1086.93 | 0 | 117.06 | 0 | 0 | 0 | 0 | 1210.41 | 82.76
2030-07-06 23:00 | 0 | 0 | 0 | 0 | 0 | 5.97 | 1.66 | 0 | 994.66 | 0 | 159.27 | 0 | 0 | 16.93 | 0 | 1178.49 | 40.55
2030-07-07 | 0 | 0 | 20 | 0 | 0 | 4.78 | 0 | 0 | 845.51 | 0 | 0 | 0 | 0 | 131.03 | 0 | 1001.32 | 319.99

## 2035 - Winter Peak
2035 Peak Load Generation
Peak Load Hour
2035-01-09 18:00
2035 | Installed Capacity (MW)
| Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
| 0 | 462 | 750 | 150 | 231 | 374.36 | 9.42 | 74.88 | 2618.87 | 142 | 153 | 459 | 0 | 360 |  | 5784.53
Generation (GWh) Jan 8, 2035 - Jan 10, 2035 | [16 empty] | Curtailed Renewables (MW)
Date/Time | Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
2035-01-08 01:00 | 0 | 127.57 | 0 | 0 | 0 | 69.04 | 2.83 | 31.8 | 1444.91 | 0 | 0 | 0 | 0 | 0 | 475 | 2151.15 | 0
2035-01-08 02:00 | 0 | 144 | 0 | 0 | 0 | 101.55 | 3.08 | 64.8 | 1024.72 | 0 | 0 | 0 | 0 | 0 | 575 | 1913.15 | 4.89
2035-01-08 03:00 | 0 | 144 | 100 | 0 | 0 | 102.28 | 2.95 | 74.8 | 736.62 | 0 | 0 | 0 | 0 | 0 | 575 | 1735.65 | 4.16
2035-01-08 04:00 | 0 | 144 | 0 | 0 | 0 | 156.13 | 1.39 | 74.8 | 884.86 | 0 | 0 | 0 | 0 | 0 | 575 | 1836.18 | 56.31
2035-01-08 05:00 | 0 | 143.26 | 250 | 0 | 0 | 69.04 | 0 | 63.12 | 660.39 | 0 | 0 | 0 | 0 | 0 | 575 | 1760.81 | 0
2035-01-08 06:00 | 0 | 144 | 700 | 0 | 0 | 80.34 | 0 | 56.36 | 218.05 | 0 | 0 | 0 | 0 | 0 | 575 | 1773.75 | 26.1
2035-01-08 07:00 | 0 | 144 | 550 | 0 | 0 | 106.44 | 1.86 | 70.92 | 572.97 | 0 | 0 | 0 | 0 | 0 | 575 | 2021.19 | 0
2035-01-08 08:00 | 0 | 144 | 550 | 0 | 0 | 318.44 | 4.24 | 74.8 | 705.28 | 0 | 192.1 | 0 | 0 | 0 | 50 | 2038.86 | 0.9
2035-01-08 09:00 | 0 | 144 | 750 | 0 | 0 | 293.69 | 5.32 | 74.8 | 421.21 | 3.98 | 175 | 0 | 0 | 0 | 300 | 2168 | 42.75
2035-01-08 10:00 | 0 | 144 | 650 | 0 | 0 | 99.59 | 4.45 | 74.8 | 526.86 | 1.36 | 182.5 | 0 | 0 | 0 | 325 | 2008.56 | 17.35
2035-01-08 11:00 | 0 | 144 | 750 | 0 | 0 | 106.44 | 0.67 | 74.8 | 505.61 | 3.65 | 172.9 | 0 | 0 | 0 | 325 | 2083.07 | 20.1
2035-01-08 12:00 | 0 | 144 | 500 | 0 | 0 | 115.04 | 0 | 74.8 | 481.6 | 9.54 | 136.88 | 0 | 0 | 0 | 425 | 1886.86 | 56.12
2035-01-08 13:00 | 0 | 144 | 600 | 0 | 0 | 142.14 | 1.38 | 64.8 | 364.6 | 2.8 | 122.26 | 0 | 0 | 0 | 425 | 1866.98 | 70.74
2035-01-08 14:00 | 0 | 144 | 500 | 0 | 0 | 135.14 | 2.83 | 74.8 | 465.15 | 2.46 | 113.34 | 0 | 0 | 0 | 450 | 1887.72 | 86.66
2035-01-08 15:00 | 0 | 174 | 700 | 0 | 0 | 320.9 | 3 | 74.8 | 425.71 | 1.77 | 188.01 | 0 | 0 | 0 | 100 | 1988.19 | 38.23
2035-01-08 16:00 | 0 | 204 | 750 | 30 | 0 | 339.14 | 2.7 | 74.8 | 242.38 | 0.84 | 122 | 30 | 0 | 0 | 450 | 2245.86 | 86
2035-01-08 17:00 | 0 | 291 | 750 | 120 | 0 | 354.14 | 1.76 | 74.8 | 140.82 | 0.01 | 175 | 141 | 0 | 194.59 | 400 | 2643.12 | 18
2035-01-08 18:00 | 0 | 291 | 750 | 120 | 0 | 354.14 | 0 | 74.8 | 97.26 | 0 | 125 | 141 | 0 | 325.05 | 400 | 2678.25 | 68
2035-01-08 19:00 | 0 | 291 | 750 | 120 | 0 | 354.14 | 1.57 | 74.8 | 180.4 | 0 | 175 | 141 | 0 | 129.63 | 350 | 2567.54 | 18
2035-01-08 20:00 | 0 | 291 | 750 | 120 | 0 | 354.14 | 4.22 | 74.8 | 275.03 | 0 | 125 | 131.67 | 0 | 0 | 400 | 2525.86 | 68
2035-01-08 21:00 | 0 | 291 | 500 | 107.92 | 0 | 354.14 | 5.3 | 74.8 | 558.47 | 0 | 125 | 64.15 | 0 | 0 | 400 | 2480.78 | 68
2035-01-08 22:00 | 0 | 285.64 | 50 | 107.92 | 0 | 248.14 | 4.22 | 74.8 | 1044.04 | 0 | 125 | 61.2 | 0 | 0 | 450 | 2450.96 | 68
2035-01-08 23:00 | 0 | 282.52 | 50 | 107.92 | 0 | 142.14 | 1.53 | 74.8 | 1043.86 | 0 | 193 | 61.2 | 0 | 0 | 350 | 2306.97 | 0
2035-01-09 | 0 | 169.68 | 0 | 52 | 0 | 102.74 | 0 | 31.8 | 1687.52 | 0 | 0 | 55 | 0 | 0 | 100 | 2198.74 | 2
2035-01-09 01:00 | 0 | 180.9 | 0 | 52 | 0 | 93.54 | 1.41 | 31.8 | 1824.63 | 0 | 0 | 55 | 0 | 0 | 100 | 2339.28 | 0
2035-01-09 02:00 | 0 | 187.72 | 0 | 52 | 0 | 93.54 | 2.38 | 31.8 | 1766.9 | 0 | 0 | 55 | 0 | 0 | 100 | 2289.34 | 0
2035-01-09 03:00 | 0 | 215.43 | 0 | 90 | 0 | 93.54 | 2.84 | 31.8 | 1412.59 | 0 | 0 | 61.2 | 0 | 0 | 100 | 2007.4 | 0
2035-01-09 04:00 | 0 | 184.76 | 0 | 52 | 0 | 93.54 | 2.83 | 31.8 | 1591.63 | 0 | 0 | 55 | 0 | 0 | 100 | 2111.56 | 0
2035-01-09 05:00 | 0 | 187.74 | 0 | 52 | 0 | 93.54 | 2.27 | 31.8 | 1500.84 | 0 | 0 | 55 | 0 | 0 | 100 | 2023.19 | 0
2035-01-09 06:00 | 0 | 241.15 | 0 | 93.42 | 0 | 116.84 | 0 | 74.8 | 916.89 | 0 | 0 | 61.2 | 0 | 0 | 575 | 2079.3 | 3.8
2035-01-09 07:00 | 0 | 291 | 300 | 107.92 | 0 | 176.94 | 0 | 74.8 | 565.01 | 0 | 0 | 98.87 | 0 | 0 | 575 | 2189.54 | 71.2
2035-01-09 08:00 | 0 | 291 | 250 | 107.92 | 0 | 232.14 | 1.69 | 74.8 | 716.35 | 0 | 156.55 | 113.52 | 0 | 0 | 325 | 2268.97 | 158.45
2035-01-09 09:00 | 0 | 291 | 300 | 107.92 | 0 | 324.02 | 4.24 | 74.8 | 587.93 | 0.21 | 193 | 122.4 | 0 | 0 | 325 | 2330.52 | 30.12
2035-01-09 10:00 | 0 | 144 | 750 | 107.92 | 0 | 328.9 | 4.96 | 74.8 | 416.31 | 0.02 | 192.89 | 0 | 0 | 100 | 325 | 2444.8 | 25.35
2035-01-09 11:00 | 0 | 144 | 750 | 112.91 | 0 | 341.14 | 4.21 | 74.8 | 370.03 | 0.69 | 193 | 0 | 0 | 264.05 | 200 | 2454.83 | 13
2035-01-09 12:00 | 0 | 144 | 750 | 107.92 | 0 | 341.14 | 1.57 | 74.8 | 345.49 | 5.61 | 193 | 0 | 0 | 174.87 | 375 | 2513.4 | 13
2035-01-09 13:00 | 0 | 144 | 300 | 107.92 | 0 | 196.57 | 0 | 74.8 | 610.07 | 12.71 | 175 | 0 | 0 | 0 | 350 | 1971.07 | 69.57
2035-01-09 14:00 | 0 | 144 | 250 | 107.92 | 0 | 201.04 | 1.75 | 74.8 | 694.13 | 10.73 | 175 | 0 | 0 | 0 | 350 | 2009.37 | 65.1
2035-01-09 15:00 | 0 | 144 | 250 | 107.92 | 0 | 313.14 | 2.63 | 74.8 | 939.51 | 16.73 | 166.96 | 0 | 0 | 0 | 100 | 2115.69 | 67.04
2035-01-09 16:00 | 0 | 144 | 750 | 0 | 0 | 341.1 | 2.81 | 74.8 | 808.52 | 0.82 | 113 | 0 | 0 | 28.17 | 100 | 2363.22 | 93.04
2035-01-09 17:00 | 0 | 144 | 650 | 0 | 0 | 232.9 | 2.63 | 74.8 | 1052.65 | 0.01 | 113 | 0 | 0 | 0 | 450 | 2719.99 | 201.24
2035-01-09 18:00 | 0 | 144 | 350 | 0 | 0 | 310.29 | 1.77 | 74.8 | 1375.68 | 0 | 113 | 0 | 0 | 0 | 400 | 2769.54 | 123.85
2035-01-09 19:00 | 0 | 144 | 550 | 0 | 0 | 218.46 | 0 | 74.8 | 1221.4 | 0 | 150 | 0 | 0 | 0 | 325 | 2683.66 | 72.68
2035-01-09 20:00 | 0 | 144 | 650 | 0 | 0 | 351.27 | 1.53 | 74.8 | 902.47 | 0 | 125 | 0 | 0 | 0 | 400 | 2649.07 | 70.87
2035-01-09 21:00 | 0 | 144 | 550 | 0 | 0 | 210.86 | 3.69 | 74.8 | 1485.53 | 0 | 113 | 0 | 0 | 0 | 50 | 2631.88 | 117.28
2035-01-09 22:00 | 0 | 144 | 0 | 0 | 0 | 132.84 | 4.59 | 74.8 | 1981.39 | 0 | 162.61 | 0 | 0 | 0 | 100 | 2600.23 | 39.69
2035-01-09 23:00 | 0 | 0 | 0 | 0 | 0 | 93.54 | 3.99 | 73.14 | 2104.67 | 0 | 113 | 0 | 0 | 0 | 0 | 2388.34 | 81.66
2035-01-10 | 0 | 0 | 20 | 0 | 0 | 83.56 | 0 | 0 | 2028.93 | 0 | 0 | 0 | 0 | 0 | 0 | 2132.49 | 140.98
2035-01-10 01:00 | 0 | 0 | 20 | 0 | 0 | 40.26 | 0 | 0 | 2034.24 | 0 | 0 | 0 | 0 | 0 | 0 | 2094.5 | 272.62
2035-01-10 02:00 | 0 | 0 | 20 | 0 | 0 | 44.51 | 0 | 0 | 2002.97 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.48 | 295.99
2035-01-10 03:00 | 0 | 0 | 20 | 0 | 0 | 42.03 | 0 | 0 | 1491.19 | 0 | 0 | 0 | 0 | 250 | 0 | 1803.22 | 788.8
2035-01-10 04:00 | 0 | 0 | 20 | 0 | 0 | 42.03 | 2.63 | 0 | 1798.11 | 0 | 0 | 0 | 0 | 100 | 0 | 1962.77 | 453.47
2035-01-10 05:00 | 0 | 53.9 | 0 | 0 | 0 | 36.44 | 2.67 | 0 | 1787.31 | 0 | 0 | 0 | 0 | 100 | 0 | 1980.32 | 482.57
2035-01-10 06:00 | 0 | 42 | 0 | 0 | 0 | 36.44 | 2.13 | 0 | 1550.94 | 0 | 0 | 0 | 0 | 260 | 0 | 1891.51 | 711.87
2035-01-10 07:00 | 0 | 42 | 0 | 0 | 0 | 37.74 | 1.22 | 0 | 2084.42 | 0 | 0 | 0 | 0 | 100 | 0 | 2265.38 | 190.94
2035-01-10 08:00 | 0 | 56.41 | 0 | 0 | 0 | 40.44 | 0 | 0 | 1850.85 | 0 | 113 | 0 | 0 | 260 | 0 | 2320.7 | 377.03
2035-01-10 09:00 | 0 | 56.41 | 0 | 0 | 0 | 36.74 | 0 | 0 | 1770.45 | 4.44 | 163.39 | 0 | 0 | 260 | 0 | 2291.43 | 450.71
2035-01-10 10:00 | 0 | 56.41 | 0 | 0 | 0 | 36.64 | 3.99 | 0 | 1909.1 | 78.8 | 113 | 0 | 0 | 100 | 0 | 2297.94 | 255.2
2035-01-10 11:00 | 0 | 0 | 0 | 0 | 0 | 50.33 | 4.22 | 0 | 2009.44 | 96.31 | 113 | 0 | 0 | 0 | 0 | 2273.3 | 297.9
2035-01-10 12:00 | 0 | 0 | 0 | 0 | 0 | 42.03 | 0 | 0 | 1542.58 | 62.44 | 113 | 0 | 0 | 260 | 0 | 2020.05 | 749.67
2035-01-10 13:00 | 0 | 0 | 0 | 0 | 0 | 58.4 | 0 | 0 | 1843.98 | 49.14 | 113 | 0 | 0 | 100 | 0 | 2164.52 | 335.25
2035-01-10 14:00 | 0 | 0 | 0 | 0 | 0 | 41.85 | 0 | 0 | 1965.61 | 70.62 | 113 | 0 | 0 | 0 | 0 | 2191.08 | 158.89
2035-01-10 15:00 | 0 | 0 | 0 | 0 | 0 | 52.63 | 1.47 | 0 | 1921.65 | 100.69 | 113 | 0 | 0 | 0 | 0 | 2189.44 | 120.81
2035-01-10 16:00 | 0 | 0 | 0 | 0 | 0 | 56.63 | 2.13 | 0 | 1785.67 | 52.35 | 142.61 | 0 | 0 | 0 | 0 | 2039.39 | 57.19
2035-01-10 17:00 | 0 | 123.55 | 0 | 0 | 0 | 81.07 | 2.48 | 10 | 1413.79 | 0.43 | 193 | 0 | 0 | 164.71 | 100 | 2089.03 | 12.52
2035-01-10 18:00 | 0 | 131.47 | 50 | 0 | 0 | 70.28 | 2.27 | 43 | 1444.69 | 0 | 193 | 0 | 0 | 289.95 | 50 | 2274.66 | 23.32
2035-01-10 19:00 | 0 | 144 | 0 | 0 | 0 | 86.79 | 1.69 | 43 | 1641.93 | 0 | 193 | 0 | 0 | 100 | 50 | 2260.41 | 6.81
2035-01-10 20:00 | 0 | 140.5 | 0 | 0 | 0 | 86.79 | 0 | 10 | 1788.49 | 0 | 193 | 0 | 0 | 70.91 | 50 | 2339.69 | 6.81
2035-01-10 21:00 | 0 | 140.5 | 0 | 0 | 0 | 72.94 | 1.57 | 43 | 1341.41 | 0 | 193 | 0 | 0 | 250 | 50 | 2092.42 | 20.66
2035-01-10 22:00 | 0 | 140.5 | 0 | 0 | 0 | 86.79 | 2.81 | 23 | 1133.5 | 0 | 193 | 0 | 0 | 253.55 | 100 | 1933.15 | 6.81
2035-01-10 23:00 | 0 | 144 | 0 | 0 | 0 | 86.79 | 3.69 | 46.44 | 918.32 | 0 | 193 | 0 | 0 | 260 | 100 | 1752.24 | 3.36
2035-01-11 | 0 | 140.5 | 50 | 0 | 0 | 86.79 | 3.62 | 43 | 936.36 | 0 | 0 | 0 | 0 | 332.29 | 100 | 1692.56 | 6.81

## 2035 - Curtailment Peak
2035 Curtailment Peak Generation
Curtailment Peak Day
2035-05-05 12:00
2035 | Installed Capacity (MW)
| Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
| 0 | 462 | 750 | 150 | 231 | 374.36 | 9.42 | 74.88 | 2618.87 | 142 | 153 | 459 | 0 | 360 |  | 5784.53
Generation (GWh) May 4, 2035 - May 6, 2035 | [16 empty] | Curtailed Renewables (MW)
Date/Time | Coal | Gas - Existing | Gas - New CTs & Recips | Gas - Conversion | Diesel CTs | Domestic Hydro | Tidal | Biomass | Wind | Solar | Maritime Link Blocks | HFO - Conversion | Hydrogen | Battery | Market Imports | Total
2035-05-04 01:00 | 0 | 0 | 0 | 0 | 0 | 137.18 | 2.75 | 43 | 801.78 | 0 | 0 | 0 | 0 | 0 | 550 | 1534.71 | 7.68
2035-05-04 02:00 | 0 | 0 | 0 | 0 | 0 | 77.71 | 0 | 43 | 1214.32 | 0 | 0 | 0 | 0 | 0 | 250 | 1585.03 | 139.35
2035-05-04 03:00 | 0 | 0 | 0 | 0 | 0 | 134.39 | 2.03 | 43 | 937.29 | 0 | 0 | 0 | 0 | 0 | 450 | 1566.71 | 10.47
2035-05-04 04:00 | 0 | 0 | 0 | 0 | 0 | 132.33 | 1.36 | 43 | 505.95 | 0 | 0 | 0 | 0 | 80.31 | 625 | 1387.95 | 12.53
2035-05-04 05:00 | 0 | 0 | 0 | 0 | 0 | 113.59 | 0.18 | 43 | 824.74 | 0 | 0 | 0 | 0 | 0 | 575 | 1556.51 | 31.27
2035-05-04 06:00 | 0 | 0 | 0 | 0 | 0 | 135.26 | 2.03 | 43 | 353.64 | 0.03 | 0 | 0 | 0 | 326.83 | 375 | 1235.79 | 9.6
2035-05-04 07:00 | 0 | 0 | 0 | 0 | 0 | 345.12 | 2.87 | 43 | 378.95 | 3.13 | 0 | 0 | 0 | 90 | 625 | 1488.07 | 11.74
2035-05-04 08:00 | 0 | 0 | 0 | 0 | 0 | 105.23 | 3.08 | 43 | 513.28 | 21.83 | 160.91 | 0 | 0 | 182.24 | 450 | 1479.57 | 44.62
2035-05-04 09:00 | 0 | 0 | 0 | 0 | 0 | 131.33 | 2.87 | 43 | 235.16 | 31.91 | 175 | 0 | 0 | 181.66 | 450 | 1250.93 | 24.78
2035-05-04 10:00 | 0 | 0 | 0 | 0 | 0 | 114.22 | 2.09 | 43 | 38.04 | 32.83 | 193 | 0 | 0 | 241.29 | 425 | 1089.47 | 30.64
2035-05-04 11:00 | 0 | 0 | 0 | 0 | 0 | 128.78 | 1.66 | 43 | 39.52 | 31.79 | 175 | 0 | 0 | 100.61 | 450 | 970.36 | 34.08
2035-05-04 12:00 | 0 | 0 | 0 | 0 | 0 | 206.62 | 1 | 43 | 44.62 | 42.62 | 175 | 0 | 0 | 60 | 450 | 1022.86 | 62.24
2035-05-04 13:00 | 0 | 0 | 0 | 0 | 0 | 183.08 | 1.81 | 43 | 25.53 | 23.26 | 175 | 0 | 0 | 90 | 450 | 991.68 | 85.78
2035-05-04 14:00 | 0 | 0 | 0 | 0 | 0 | 350.08 | 2.37 | 43 | 26.71 | 17.74 | 125 | 0 | 0 | 0 | 500 | 1064.9 | 74.78
2035-05-04 15:00 | 0 | 0 | 0 | 0 | 0 | 131.33 | 2.41 | 43 | 28.28 | 17.21 | 125 | 0 | 0 | 77.65 | 500 | 924.88 | 74.78
2035-05-04 16:00 | 0 | 0 | 0 | 0 | 0 | 350.08 | 1.65 | 43 | 38.3 | 7.85 | 125 | 0 | 0 | 90 | 500 | 1155.88 | 74.78
2035-05-04 17:00 | 0 | 143.18 | 250 | 0 | 0 | 350.08 | 0.57 | 43 | 36.96 | 2.43 | 125 | 0 | 0 | 0 | 500 | 1451.22 | 74.78
2035-05-04 18:00 | 0 | 144 | 0 | 0 | 0 | 350.08 | 0.9 | 43 | 41.21 | 1.61 | 125 | 0 | 0 | 327.43 | 500 | 1533.23 | 74.78
2035-05-04 19:00 | 0 | 144 | 0 | 0 | 0 | 350.08 | 2.09 | 43 | 40.59 | 0.04 | 150 | 0 | 0 | 331.1 | 475 | 1535.9 | 49.78
2035-05-04 20:00 | 0 | 144 | 0 | 0 | 0 | 335.08 | 2.87 | 43 | 52.82 | 0 | 175 | 0 | 0 | 307.84 | 450 | 1510.61 | 39.78
2035-05-04 21:00 | 0 | 144 | 0 | 0 | 0 | 350.08 | 2.88 | 43 | 112.09 | 0 | 175 | 0 | 0 | 260 | 450 | 1537.05 | 24.78
2035-05-04 22:00 | 0 | 144 | 0 | 0 | 0 | 348.5 | 1.87 | 43 | 272.03 | 0 | 150 | 0 | 0 | 90.42 | 475 | 1524.82 | 51.36
2035-05-04 23:00 | 0 | 61.78 | 0 | 0 | 0 | 93.93 | 0.06 | 43 | 783.35 | 0 | 119.09 | 0 | 0 | 0 | 325 | 1426.21 | 80.69
2035-05-05 | 0 | 57.66 | 0 | 0 | 0 | 92.23 | 0 | 43 | 968.14 | 0 | 0 | 0 | 0 | 0 | 150 | 1311.03 | 79.76
2035-05-05 01:00 | 0 | 132.2 | 200 | 0 | 0 | 61.33 | 2.66 | 43 | 1000.56 | 0 | 0 | 0 | 0 | 0 | 150 | 1589.75 | 783.1
2035-05-05 02:00 | 0 | 144 | 0 | 0 | 0 | 75.22 | 2.09 | 43 | 1117.45 | 0 | 0 | 0 | 0 | 0 | 150 | 1531.76 | 1060.31
2035-05-05 03:00 | 0 | 140.5 | 750 | 0 | 0 | 61.38 | 0 | 43 | 348.08 | 0 | 0 | 0 | 0 | 0 | 150 | 1492.96 | 1923.88
2035-05-05 04:00 | 0 | 144 | 0 | 0 | 0 | 89.23 | 0.59 | 43 | 1049.86 | 0 | 0 | 0 | 0 | 0 | 150 | 1476.68 | 1073.03
2035-05-05 05:00 | 0 | 144 | 0 | 0 | 0 | 107.53 | 0 | 43 | 322.17 | 0 | 0 | 0 | 0 | 350 | 150 | 1116.7 | 1479.84
2035-05-05 06:00 | 0 | 123.55 | 0 | 0 | 0 | 157.58 | 0 | 43 | 305.99 | 8.71 | 0 | 0 | 0 | 350 | 150 | 1138.83 | 1904.59
2035-05-05 07:00 | 0 | 144 | 0 | 0 | 0 | 163.79 | 2.03 | 43 | 961.23 | 54.67 | 0 | 0 | 0 | 0 | 150 | 1518.72 | 1422.37
2035-05-05 08:00 | 0 | 140.5 | 0 | 0 | 0 | 44.23 | 1.81 | 43 | 926.71 | 22.26 | 193 | 0 | 0 | 0 | 150 | 1521.51 | 1464.36
2035-05-05 09:00 | 0 | 144 | 500 | 0 | 0 | 61.09 | 0 | 43 | 134.49 | 30.88 | 113 | 0 | 0 | 260 | 150 | 1436.46 | 2209.54
2035-05-05 10:00 | 0 | 140.5 | 0 | 0 | 0 | 176.83 | 0 | 43 | 1032.04 | 0.32 | 193 | 0 | 0 | 0 | 150 | 1735.69 | 1347.9
2035-05-05 11:00 | 0 | 144 | 0 | 0 | 0 | 106.28 | 0 | 43 | 389.58 | 0 | 193 | 0 | 0 | 350 | 150 | 1375.86 | 1972.94
2035-05-05 12:00 | 0 | 140.5 | 0 | 0 | 0 | 70.71 | 0 | 43 | 380.73 | 122.51 | 113 | 0 | 0 | 322.35 | 150 | 1342.8 | 1994.88
2035-05-05 13:00 | 0 | 140.5 | 0 | 0 | 0 | 77.7 | 0 | 43 | 919.19 | 120.65 | 193 | 0 | 0 | 0 | 150 | 1644.04 | 1396.68
2035-05-05 14:00 | 0 | 140.5 | 0 | 0 | 0 | 68.73 | 0 | 43 | 945.73 | 122 | 113 | 0 | 0 | 0 | 150 | 1582.96 | 1520.57
2035-05-05 15:00 | 0 | 144 | 0 | 0 | 0 | 119.65 | 0 | 43 | 137.08 | 125.83 | 176.21 | 0 | 0 | 348.03 | 150 | 1243.8 | 2211.92
2035-05-05 16:00 | 0 | 144 | 0 | 0 | 0 | 71.58 | 0.19 | 43 | 923.44 | 0.99 | 193 | 0 | 0 | 0 | 150 | 1526.2 | 1178.63
2035-05-05 17:00 | 0 | 140.5 | 0 | 0 | 0 | 106.09 | 0 | 43 | 164.51 | 71.69 | 176.68 | 0 | 0 | 350 | 150 | 1202.47 | 1634.44
2035-05-05 18:00 | 0 | 140.5 | 0 | 0 | 0 | 133.86 | 0 | 43 | 216.58 | 14.49 | 113 | 0 | 0 | 350 | 150 | 1161.43 | 1570.85
2035-05-05 19:00 | 0 | 144 | 0 | 0 | 0 | 55.53 | 2.34 | 43 | 975.14 | 24.54 | 126.67 | 0 | 0 | 0 | 150 | 1521.22 | 462.83
2035-05-05 20:00 | 0 | 144 | 0 | 0 | 0 | 99.53 | 0 | 43 | 201.81 | 0 | 193 | 0 | 0 | 350 | 150 | 1181.34 | 1016.77
2035-05-05 21:00 | 0 | 140.5 | 0 | 0 | 0 | 161.14 | 1.81 | 43 | 737.1 | 0 | 132.44 | 0 | 0 | 90 | 150 | 1455.99 | 603.17
2035-05-05 22:00 | 0 | 123.55 | 400 | 0 | 0 | 55.77 | 0 | 43 | 12.51 | 0 | 113 | 0 | 0 | 318.5 | 150 | 1216.33 | 1878.57
2035-05-05 23:00 | 0 | 144 | 0 | 0 | 0 | 90.68 | 1.66 | 43 | 1012.2 | 0 | 113 | 0 | 0 | 0 | 150 | 1554.54 | 1043.23
2035-05-06 | 0 | 144 | 0 | 0 | 0 | 112.55 | 0 | 43 | 347.87 | 0 | 0 | 0 | 0 | 350 | 150 | 1147.42 | 1960.67
2035-05-06 01:00 | 0 | 42 | 0 | 0 | 0 | 51.53 | 3.59 | 0 | 1346.78 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.9 | 751.54
2035-05-06 02:00 | 0 | 42 | 0 | 0 | 0 | 60.83 | 3.66 | 0 | 1306.46 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.95 | 918.37
2035-05-06 03:00 | 0 | 56 | 0 | 0 | 0 | 50.53 | 0 | 0 | 1112.29 | 0 | 0 | 0 | 0 | 90 | 0 | 1308.82 | 450.56
2035-05-06 04:00 | 0 | 56 | 0 | 0 | 0 | 59.63 | 0 | 0 | 756.06 | 0 | 0 | 0 | 0 | 255.42 | 0 | 1127.11 | 534.08
2035-05-06 05:00 | 0 | 50.49 | 0 | 0 | 0 | 60.93 | 0 | 0 | 849.7 | 0 | 0 | 0 | 0 | 180 | 0 | 1141.12 | 231.91
2035-05-06 06:00 | 0 | 42 | 0 | 0 | 0 | 75.78 | 1.87 | 0 | 1089.13 | 0.23 | 0 | 0 | 0 | 90 | 0 | 1299.01 | 123.8
2035-05-06 07:00 | 0 | 0 | 0 | 0 | 0 | 67.58 | 2.41 | 0 | 1006.13 | 1.49 | 0 | 0 | 0 | 90 | 100 | 1267.61 | 244.59
2035-05-06 08:00 | 0 | 0 | 0 | 0 | 0 | 94.47 | 2.61 | 0 | 891.38 | 27.88 | 193 | 0 | 0 | 0 | 0 | 1209.34 | 6.78
2035-05-06 09:00 | 0 | 0 | 0 | 0 | 0 | 67.31 | 2.29 | 0 | 208.74 | 3.37 | 148.37 | 0 | 0 | 335 | 0 | 765.08 | 397.17
2035-05-06 10:00 | 0 | 0 | 0 | 0 | 0 | 64.63 | 0 | 0 | 257.04 | 14.62 | 135.64 | 0 | 0 | 260 | 0 | 731.93 | 305.34
2035-05-06 11:00 | 0 | 0 | 0 | 0 | 0 | 60.83 | 0 | 0 | 454.41 | 22.9 | 193 | 0 | 0 | 90 | 0 | 821.14 | 996.45
2035-05-06 12:00 | 0 | 0 | 0 | 0 | 0 | 58.26 | 0 | 0 | 133.78 | 26.94 | 113 | 0 | 0 | 260 | 0 | 591.98 | 2406.29
2035-05-06 13:00 | 0 | 0 | 0 | 0 | 0 | 51.53 | 0 | 0 | 675.06 | 17.62 | 134.99 | 0 | 0 | 0 | 0 | 879.2 | 1263.19
2035-05-06 14:00 | 0 | 0 | 0 | 0 | 0 | 65.82 | 0 | 0 | 55.58 | 17.64 | 113 | 0 | 0 | 335 | 0 | 587.04 | 1884.17
2035-05-06 15:00 | 0 | 0 | 0 | 0 | 0 | 60.64 | 0 | 0 | 327.65 | 25.33 | 113 | 0 | 0 | 260 | 0 | 786.62 | 1697.32
2035-05-06 16:00 | 0 | 0 | 0 | 0 | 0 | 60.83 | 0 | 0 | 789.76 | 13.22 | 113 | 0 | 0 | 100 | 0 | 1076.81 | 1113.62
2035-05-06 17:00 | 0 | 0 | 0 | 0 | 0 | 54.89 | 0 | 0 | 1166.38 | 19.89 | 193 | 0 | 0 | 0 | 0 | 1434.16 | 396.32
2035-05-06 18:00 | 0 | 0 | 0 | 0 | 0 | 63.47 | 0 | 0 | 1165.75 | 20.48 | 193 | 0 | 0 | 100 | 0 | 1542.7 | 479.08
2035-05-06 19:00 | 0 | 0 | 0 | 0 | 0 | 60.3 | 2.29 | 0 | 928.54 | 2.52 | 193 | 0 | 0 | 260 | 0 | 1446.65 | 85.24
2035-05-06 20:00 | 0 | 0 | 0 | 0 | 0 | 60.93 | 0 | 0 | 1013.32 | 0 | 113 | 0 | 0 | 260 | 0 | 1447.25 | 432.24
2035-05-06 21:00 | 0 | 0 | 0 | 0 | 0 | 64.61 | 2.75 | 0 | 1279.7 | 0 | 193 | 0 | 0 | 92.37 | 0 | 1632.43 | 96.12
2035-05-06 22:00 | 0 | 0 | 0 | 0 | 0 | 60.83 | 0 | 0 | 1016.41 | 0 | 113 | 0 | 0 | 260 | 0 | 1450.24 | 346.9
2035-05-06 23:00 | 0 | 0 | 0 | 0 | 0 | 161.26 | 1.08 | 0 | 972.7 | 0 | 193 | 0 | 0 | 100 | 0 | 1428.04 | 79.98
2035-05-07 | 0 | 0 | 0 | 0 | 0 | 45.63 | 0 | 0 | 680.15 | 0 | 0 | 0 | 0 | 345 | 100 | 1170.78 | 340.88