## IR-57
Downline Connectivity
Region | Area / Community | Feeder / Substation (part of) | Feeders | Condition | Criticality | Risk | Key Risk Factors
West | Three Mile Plains | 79V-401 | 79V-401 | 4 | 4 | 16 | Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
Metro | Musquodoboit Harbour | 87H-313 | 87H-313 | 5 | 5 | 25 | Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
Metro | Musquodoboit Harbour | 87H-313 | 87H-313 | 5 | 5 | 25 | Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
Northeast | Dickie Brook | 24C-442 | 24C-442 | 5 | 5 | 25 | Historically a problem feeder. Long, rural feeder in area with small crew compliment, resulting in extended reponse times.
Northeast | Ruth Falls | 96H-412 | 96H-412 | 5 | 4 | 20 | Historical reliability performance issues. Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
Northeast | Ruth Falls | 96H-412 | 96H-412 | 5 | 4 | 20 | Historical reliability performance issues. Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
Northeast | Ruth Falls | 96H-412 | 96H-412 | 5 | 4 | 20 | Historical reliability performance issues. Long, rural feeder in area with small crew compliment, resulting in extended reponse times. High average customer count.
West | Waterville | 55V-313 | 55V-313 | 4 | 4 | 16 | Long, rural feeder resulting in extended response times. High average customer count.
Metro | Lucasville | 131H-422 | 131H-422 | 4 | 5 | 20 | Historical feeder reliability performance issues. Elevated feeder loading. High customer density.
Cape Breton | Ingonish & Cape North | 85S-401 | 85S-401 | 5 | 5 | 25 | Long, remote rural radial feeder with challenging terrain, persistent vegetation and weather‑related exposure, and historically poor reliability performance (elevated CKAIFI/CKAIDI).
Cape Breton | Coxheath & Eskasoni | 11S-411 | 11S-411 | 4 | 5 | 20 | Remote rural radial feeder with no alternate supply, recurring vegetation and equipment‑related fault drivers, and documented reliability performance challenges under geographic and operational constraints.
Metro | Lakeside | 103H | 103H-433 | 2 | 4 | 8 | Critical backbone feeder with high customer count and complex network topology, where faults result in significant service impact and operational complexity.
Metro | Kearney Lake | 129H | 129H-412 | 4 | 4 | 16 | High‑growth, high‑density feeder exposed to motor vehicle and construction incidents, with traffic congestion limiting crew response despite access to alternative supply sources.
Metro | Hammonds Plains | 137H | 137H-414 | 3 | 5 | 15 | Feeder serving a rapidly growing, increasingly dense area with historical reliability performance concerns (CKAIFI), where interruptions carry higher customer impact despite multiple available feeder ties.
Metro | Armdale | 2H | 2H-411 | 4 | 4 | 16 | High‑density urban backbone feeder with a large and growing customer base, limited redundancy, and constrained sectionalization capability, resulting in elevated outage consequence as loading increases.
Metro | Armdale | 2H | 2H-421 | 4 | 4 | 16 | Complex urban feeder serving a dense customer area where outages have high impact; proximity to adjacent feeders provides some operational flexibility but does not materially reduce consequence of failure.
Metro | Kempt Rd | 104H | 104H-423 | 4 | 4 | 16 | Urban feeder exposed to congestion and frequent construction activity, increasing disturbance and fault risk despite availability of alternative power flow sources.
Metro | Kempt Rd | 104H | 104H-433 | 3 | 4 | 12 | High‑density urban backbone feeder with complex topology and elevated third‑party damage risk, resulting in high outage consequence and operational complexity.