## Sheet1
Investment Track | Sub-Program | SAIDI per $M Notes
Storm Hardening - Vegetation Management | Distribution Corridor Widening with Managed Rights-of-Way (ROW) | Based on historical performance results of tree contact CHI, comprehensive and proactive vegetation management has demonstrated a materially higher impact on reducing tree‑contact‑related outages during Major Event Days (MEDs), relative to observed improvements of approximately 25% under System Event Days (SEDs) and Normal Operating Conditions. Program cost assumptions and expected benefits have been developed using historical project costs and validated through post‑implementation performance assessments.
Storm Hardening - Vegetation Management | Establish New Rights-of-Way (ROW)
Storm Hardening - Vegetation Management | Trimming and Removal of Trees Around Existing Power Lines
Storm Hardening - Targeted Equipment Replacement and Upgrades | Distribution System Equipment Upgrades and Replacements | Calculations were based on a improvement to defective equipment outages CHI with targeted device types. Includes assets addressed through accelerated (quick‑cycle) interventions rather those requiring more complex replacement programs, to ensure alignment with execution constraints and timelines.
Storm Hardening - Targeted Equipment Replacement and Upgrades | Build-to-Roadside Program | Average percentage contribution to defective equipment CHI from off-road sections assumes improvement in defective equipment reliability experienced by sections move to roadside along with reduction in average percentage contribution to tree contacts from off-road sections. Assessment of these available sections and potential reduction in CHI.
Storm Hardening - Targeted Equipment Replacement and Upgrades | Distribution System Conductor Upgrades | This program targets conductor deficiencies identified through inspection programs, with reduction estimates derived from historical outage data specific to conductor failures. Historical performance indicates that, with appropriate prioritization of higher‑risk feeders, these interventions can result in approximately one avoided outage every three years per treated section, on average.
Storm Hardening - Targeted Equipment Replacement and Upgrades | Distribution System Underground Upgrades | This initiative focuses on outage drivers linked to water ingress and feeder exit cable failures. Assessed improvement of CHI with limited historical data, the quantified improvement potential is inherently constrained and subject to higher uncertainty.
Advanced Grid Modernization Programs | Remote Terminal Units (RTUs) | CHI improvement estimates for automation initiatives are applied to the annual average of full‑feeder outage events. The analysis is limited to feeders and locations without existing Remote Terminal Units (RTUs) and excludes outage categories not affected by automation (e.g., loss of supply, planned outages). Costs and benefits associated with RTU deployments are captured within the dedicated RTU program. Where feasible, communication upgrades to existing substation devices (e.g., reclosers) are recognized as part of this scope and delivers comparable operational benefits by leveraging existing infrastructure.
Advanced Grid Modernization Programs | Downline Connectivity | The CHI impact is estimated based on the location of the new protection device, adjusting the proportion of customers affected by the share of line downstream. For example, a midpoint recloser corresponds to an approximate 25% reduction in CHI from full feeder‑section outages. For branch line protection, the estimate requires assumptions regarding transient faults that could otherwise result in broader outages. This can be assessed by considering outage causes associated with transient events (e.g., vegetation, animals, wind) and applying a corresponding reduction factor. Historical assessments have also applied an assumed restoration time improvement (e.g., ~15 minutes per event) for downstream customers based on average feeder interruption frequency.
Advanced Grid Modernization Programs | Fault Location Isolation and Service Restoration (FLISR)